## CONTENT
TAB | Content
VF_ch | The characteritics of the VF to calculate the cooling and reheating demands of the cooling and dehumidification system.
VF_CDS | Energy performance calculations of the baseline cooling and dehumidification system of the VF (standalone VF)
Int_A1 | Integration VF within the heat system of the host-building using direct integration strategy A1: HE (Section 2.3.1)
Int_B1 | Integration VF within the heat system of the host-building using direct integration strategy B1: HP (Section 2.3.1)
Int_E2 | Integration VF within the heat system of the host-building using integration strategy E2: HP+HP+ATES (Section 2.3.2)
BS_Ap | Baseline energy use for heating and cooling 80m2 apartments with energy label BENG, A or C when using an air-source HP
BS_off | Baseline energy use for heating and cooling small and large offices with energy label BENG, A or C when using an air-source HP
BS_res | Baseline energy use for heating and cooling a restaurant when using an air-sourced HP
BS_Sw | Baseline energy use for heating the indoor and outdoor swimming pool when using an air-sourced HP

## VF_ch
Energy characteristics VF
Supply | 24 | C | 76% | RH
Return | 26 | C | 72% | RH
Light qualities
PPFD | 200 | μmol s-1 m-2
Photoperiod | 16 | h
molar efficacy | 3.5 | μmol J−1 | Weidner et al., 2021
DLI | 11.52 | mol m-2 d-1
Energy use LED and heat production
Watt per m2 | 57.1429 | W m-2
LED usage | 333.7143 | kWh m-2 y-1
Heat dissipated LED | 90%
cooling loads LED light | 300.3429 | kWh m-2 y-1
Qcooling | 1081.2343 | MJ m-2 y-1
Qcooling | 51.4286 | J m-2 s-1
Cooling and dehumidification
Psychrometric chart properties |  |  |  | http://www.flycarpet.net/en/psyonline
Point 1 |  |  |  | Point 2 |  |  | Point 3
Temperature T1 | 26 | C |  | Temperature T2 | 19.511 | C | Temperature T3 | 24 | C
R.H. 1 | 0.72 |  |  | R.H. 2 | 1 |  | R.H. 3 | 0.76
enthalphy h1 | 65.109 | kJ/kg |  | enthalphy h2 | 55.903 | kJ/kg | enthalphy h3 | 60.531 | kJ/kg
humidity ratio w 1 | 0.01529 | kg/kg |  | humidity ratio w2 | 0.014303 | kg/kg | humidity ratio w3 | 0.014303 | kg/kg
Specific volume v1 | 1.026 | m3/kg |  | Specific volume v2 | 0.848 | m3/kg | Specific volume v3 | 0.861 | m3/kg
Air density P1 | 1.169 | kg/m3 |  | Air density p2 | 1.196 | kg/m3 | Air density p3 | 1.178 | kg/m3
Specific heat Cpa 1 | 1026 | J/kg K |  |  |  |  | Specific heat Cpa 3 | 1025 | J/kg K
Data per m2 cultivation area:
Qvf (point 3 -> 1)
Qtot = Qs + Ql | 0.051429 | kJ/s
Qs = Cpa * ma * dT | 0.024218 | kJ/s
Ql = ma * hw *dw =mw * hw | 0.027211 | kJ/s
ma = Qtot / dh | 0.011234 | kg/s
hwe latent heat evaporization water | 2454.1 | kJ/kg
Cpa in VF | 1077.9016 | J/kg K
Qout
Qout = Qs,out + Ql,out
Qout;tot = ma * (h2-h1) | -0.10342 | kJ/s
Qs = Cp * ma *dT = Qtot - Ql | -0.076208 | kJ/s
Ql = ma * (w2-w1) * hw | -0.027211 | kJ/s
hwe | 2454.1 | kJ/kg | at T water
T dewpoint | 20.563 | C
Twater = (T DPT + T2) /2 | 20.037 | C
m water removed from system:
mw = ma * (w1-w2) | 1.1088e-05 | kg/s
Qin
Qin;tot = ma * (h3-h2) | 0.05199 | kJ/s
Qs = Qtot - Ql | 0.05199 | kJ/s
Ql = Qlatent = ma * (w3-w2) * hv | 0 | kJ/s | w2=w3
Energy balance
Eheat VF = Qout + Qin | -0.051429 | kJ/s
Esensible VF = Es out + Es in | -0.024218 | kJ/s
Elatent VF = El;out + El in | -0.027211 | kJ/s
Qtot VF | -0.051429 | kJ/s
RESULTS
| Qs | Ql | Qtot
| J s-1 m-2 | J s-1 m-2 | J s-1 m-2
Qvf | +24.2 | +27.2 | +51.4
Qout | -76.2 | -27.2 | -103.4
Qin | +52.0 | 0.0 | +52.0

## VF_CDS
Baseline cooling and dehumidification system
HE1
air/water HE - dehumidification and cooling below DPT (Appendix B.1.1)
Qtot air-side = (h2-h1) * mair | -0.10342 | kJ/s | equal to Qout
Qs air-side | -0.076208 | kJ/s | equal to Qout;s
Ql air-side | -0.027211 | kJ/s | equal to Qout;l
ma | 0.011234 | kg/s
Qhe1 | -0.10342 | kJ/s
Cpw | 4184 | J/kg K
mw | -0.0045774 | kg/s
ε - Effectiveness HE (%)
ε = (Tc,o - Tc,i)/(Th,i - Tc,i) | 70% | air-water HE counterflow |  |  | Appendix B.1.1.
Tc,i = Tw,i | 16.73 | C |  |  | Appendix B.1.1. - Eq. B.5
Tc,o = Tw,o | 22.13 | C |  |  | see evaporator
Th,i= Ta,i | 26 | C
Th,o = Ta,o | 19.511 | C |  |  | Temp 2 (VF_ch)
HP1
Condenser
ε = (Tc,o - Tc,i) / (Th- Tc,i ) | 90% |  | Appendix B3.1
Qc = mw * Cpw * dT | 0.11237 | kJ/s
Tc,i | 24 | C | Temp 2 (VF_ch)
Tc,o | 31.2 | C
Th,i = Th,o = Tcon = T1 | 32 | C | Selected
TD = Th - Tc,i | 8 | C
Evaporator
Qhot = mh * Ch * dT | -0.10342 | kJ/s
Qcold | 0.10342 | kJ/s
ε = (Th,i - Th,o) / (Th,i - Tc) | 90% |  | Appendix B3.1
Th,i = Thot in | 22.13 | C
Th,o = Thot, out | 16.73 | C | Tc,i HE1
Tc,i = Tc, o = T3 | 16.13 | C
TD = Th,i - Tc | 6 | C
Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K) |  | Appendix B3.2
1 - Saturated liquid (100%): subcooling | 32 | 8.1628 | 244.8
2 - liquid + vapour | 16.13 | 5.0631 | 244.8
3 - Saturated vapour (100%): superheat | 16.13 | 5.0631 | 407.86 | 1.7204
4 -liquid + vapour: highly superheated | 33.5993 | 8.1628 | 417.7373 | 1.7204
Isentropic efficiency E
E = (h4 - h3) / (h4' - h3) | 70% |  |  | Appendix B3.2
h4' | 421.9705 | kJ/kg
P4' | 8.1628 | bar
Qcold = Qev
Qcold = m * (h3-h2) | -0.10342 | kJ/s
ṁr = flow rate refrigerant | -0.00063424 | kg/s
ṁ water through evaporator | 0.0045774 | kg/s
Qhot = Qcon
Q = mw * Cpw * dT | 112.3682 | J/s
mw = mf | 0.0037301 | kg/s
Qhot = mr * (h1-h4') | 0.11237 | kJ/s
ṁr = flow rate refrigerant | -0.00063424 | kg/s
COP cooling
COPhp = (h4'-h1)/(h4'-h3) | 12.5559
Win = Qcon / COPhp | 0.0089494 | kJ/s
Win = m *dh | 0.0089494 | kJ/s
COPref = (h3-h2) / (h4' - h3) | 11.5559
Win = Qev / COPref | 0.0089494 | kJ/s
HE2 | [6 empty] | HE2
air-to-water HE, reheating
Qhe = ma * (h3-h2) | 0.05199 | kJ/s
Qs = mw * Cpw * dT
mw | 0.0022699 | kg/s
ε = (Th,o - Th,I) / (Th,i - Tc,i) | 70% |  | Appendix B1.2, Equation B.10
Tc,i | 19.511 | C | Temp 2 (VF_ch)
Tc,o | 24 | C | Temp 3 (VF_ch)
Th,i | 27.3313 | C | mixing value 2
Th,o | 21.8571 | C
Qs air-side =- Qs water-side | -0.05199 | kJ/s
Cpw | 4184 | J/kg K
mixing valve 2
Qhe2 = ml * Cpw * (Ti - Th) | 51.9903 | J/s
(Qhe2/CPw)/Tf | 3.3313
Th,i | 27.3313 | C
ml = (Th - Tf) / (Th - Tl) * mf | 0.0022699 | kg/s | Appendix B2
Tl (low) | 21.8571 | C
Th | 27.3313 | C | Th,i HE2
mf | 0.0037301 | kg/s
Tf | 24 | C | Tc,i condenser
mh = mf - ml | 0.0014602 | kg/s
HE3
water-to-air, removes residual heat
Qhe3= mw4b * Cw * dT
Qhe3 = Qcon - Qhe2 | 0.060378 | kJ/s | 352.6074 | kWh m-2 y-1
ε = (Th,o - Th,I) / (Th,i - Tc,i) | 70% |  |  | Appendix B1.3
Tc,i | 11 | C |  | Average ambient temperature NL
Tc,o | 25 | C |  | Selected temperature
Th,i | 31.2 | C |  | Tc,o condenser
Th,o | 17.06 | C
Qs air-side =- Qs water-side | 60.378 | J/s |  | as no heat losses
mw2c | -0.0010206 | kg/s
ma 2 | 0.0042913 | kg/s
Mixing valve 3
ml = (Th - Tf) / (Th - Tl) * mf
ml = mass flow low temperature in | 0.0010206 | kg/s
tl = low temperature in | 17.06 | C |  | Th,o HE3
th | 31.2 | C |  | Tc,o condenser
mf | 0.0037301 | kg/s
tf | 27.3313 | C |  | Th,i HE2
mh = mf - ml | 0.0027095 | kg/s
Energy use pumps
| unit | Pump HE1-Ev | Pump HE2 - con |  | Appendix B.4.1., formulae B.22-B.24
Head | m | 3 | 3 |  | Appendix B.4.1.
dP (average pressure difference) | bar | 0.294 | 0.294
flow rate | kg/s | 0.0045774 | 0.0037301
Capacity | m3/s | 4.5911e-06 | 3.7413e-06
n pump | % | 72% | 72% |  | Kaya et al., 2021
Epump | kWh | 1.0948 | 0.89218
p water | 997 | kg/m3
h active | 5840 | hrs/yr
Energy use fans
| unit | Indoor fan VF | Fan outdoor unit |  | Appendix B.4.2., formulae B.25-B.27
Air density | kg/m3 | 1.225 | 1.225
Uair ducts (not farm) | m/s max | 8 | 6
Friction loss | Pa | 256.8 | 151.8
Pressure difference | Pa | 296 | 173.85
Vair | kg/s | 0.011234 | 0.0042913
Vair | m3/s | 0.0091705 | 0.0035031
n fan | % | 65% | 65% |  | Graamans et al., 2020
E fan | kWh | 24.3884 | 5.4717
velocity | m/s | 8 | 6 |  | Appendix B.4.2.
COSP - coefficient of system performance
| J s-1 | kWh m-2 y-1
E HP | 8.9494 | 52.2646
Epump | 0.34024 | 1.987
Efans | 5.113 | 29.8601
Etot | 14.4027 | 84.1117
1
2
4'
3
dH = -Ws
3'
4

## Int_A1
Direct integration strategy A1: HE
HE3
water-to-water HE
Qhe = ma * (h3-h2) | 0.060378 | kJ/s
mw | 0.0021998 | kg/s |  | Qs = mw * Cpw * dT
ε = (Th,i - Th,o)/(Th,i - Tc,i) | 80%
Tc,i | 23 | C | swimming pool return
Tc,o (water temp to building HP) | 29.56 | C | swimming pool supply
Th,i | 31.2 | C | Condenser HP2 out
Th,o (exhaust air temperature) | 24.64 | C
Mixing valve 3
ml = (Th - Tf) / (Th - Tl) * mf
ml | 0.0021998 | kg/s
tl | 24.64 | C | Th,o HE3
th | 31.2 | C | Th,i HE3
mf | 0.0037301 | kg/s
tf | 27.3313 | C
mh | 0.0015303 | kg/s
Energy use pumps
Energy use pumps within VF system | 0.34024 | J/s | VF_CDS
Energy use fans
Energy use fans within VF system | 4.1761 | J/s | VF_CDS: not including the outdoor unit
COSP - coefficient of system performance
Etotal indoor pool | J s-1 | kWh m-2 y-1
E HP | 8.9494 | 52.2646
Epump | 0.34024 | 1.987
Efans | 4.1761 | 24.3884
Etot | 13.4658 | 78.64
COSPr = Qtot VF / Etot | 3.8192
h active | 5840 | hrs/yr
Etotal outdoor pool | J s-1 | kWh m-2 y-1
E HP | 8.9494 | 21.8366
Epump | 0.34024 | 0.83019
Efans | 4.1761 | 10.1897
Etot | 13.4658 | 32.8564
COSPr = Qtot VF / Etot | 3.8192
h active | 2440 | hrs/yr

## Int_B1
Direct integration strategy B1: HP
HP2
Condenser
ε = (Tc,o - Tc,i) / (Th- Tc,i ) | 90%
| LT heat | MT heat | Swimming pool
Tc,i | 30 | 50 | 23 | C
Tc,o | 40 | 70 | 30 | C
Th,i = Th,o = Tcon = T1 | 41.1111 | 72.2222 | 30.7778 | C
TD | 11.1111 | 22.2222 | 7.7778 | C | TD MT high due to high dT radiators
Evaporator
ε = (Th,i - Th,o) / (Th,i - Tc,i) | 90%
| LT heat | MT heat | Swimming pool
Th,i = Thot in | 31.2 | 31.2 | 31.2 | C | VF_CDS HE3 Th,i
Th,o = Thot, out | 17.06 | 17.06 | 17.06 | C | VF_CDS HE3 Th,o
Tc,i = Tc, o (T3) | 15.4889 | 15.4889 | 15.4889 | C
TD | 1.5711 | 1.5711 | 1.5711 | C
LT Heat
Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K)
1 - Saturated liquid (100%): subcooling | 41.1111 | 10.4797 | 258.25
2 - liquid + vapour | 15.4889 | 4.9673 | 258.25
3 - Saturated vapour (100%): superheat | 15.4889 | 4.9673 | 407.55 | 1.7206
4 -liquid + vapour: highly superheated | 41.794 | 10.4797 | 423.0051 | 1.7206
MT heat
Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K)
1 - Saturated liquid (100%): subcooling | 72.2222 | 22.2351 | 308.66
2 - liquid + vapour | 15.4889 | 4.9673 | 308.66
3 - Saturated vapour (100%): superheat | 15.4889 | 4.9673 | 407.55 | 1.7206
4 -liquid + vapour: highly superheated | 77.9609 | 22.2351 | 438.2373 | 1.7206
Swimming pool
Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K)
1 - Saturated liquid (100%): subcooling | 30.7778 | 7.8895 | 243
2 - liquid + vapour | 15.4889 | 4.9673 | 243
3 - Saturated vapour (100%): superheat | 15.4889 | 4.9673 | 407.55 | 1.7206
4 -liquid + vapour: highly superheated | 32.3137 | 7.8895 | 417.0715 | 1.7206
Isentropic efficiency E
E = (h4 - h3) / (h4' - h3) | 70%
| LT heat | MT heat | Swimming pool
h4' | 429.6287 | 451.389 | 421.1521 | kJ/kg
Qcold = Qev | 0.060378 | 0.060378 | 0.060378 | kJ/s
Qhe3= mw4b * Cw * dT
dT | -14.14 | -14.14 | -14.14 | C
mw4b = mw4 - mw4a | 0.0010206 | 0.0010206 | 0.0010206 | kg/s
Qcold = m * (h3-h2) | -0.060378 | -0.060378 | -0.060378 | kJ/s
ṁr = flow rate refrigerant | -0.00040441 | -0.00061056 | -0.00036693 | kg/s
Qhot = Qcon
Qhot = mr * (h1-h4') | 0.069307 | 0.087144 | 0.065369 | kJ/s
ṁr = flow rate refrigerant | -0.00040441 | -0.00061056 | -0.00036693 | kg/s
Cp water | 4184 | 4184 | 4184 | J/ kg K
ṁ water through condenser | 0.0016565 | 0.0010414 | 0.0022319 | kg/s
COP
COPhp = Qcon/Win | 7.7622 | 3.2558 | 13.0974
Win = Qcon / COPhp | 0.0089288 | 0.026766 | 0.004991 | kJ/s
COPref | 6.7622 | 2.2558 | 12.0974
Win = Qev / COPref | 0.0089288 | 0.026766 | 0.004991 | kJ/s
Energy use pumps
Energy use pumps within VF system | 0.34024 | J/s | VF_CDS
Energy use fans
Energy use fans within VF system indoor | 4.1761 | J/s | VF_CDS: not including the outdoor unit
COSP
LT Heating | J m-2 s-1 | kWh m-2 y-1
E HP | 17.8782 | 43.6228
Epump | 0.34024 | 0.83019
Efans | 4.1761 | 10.1897
Etot | 22.3945 | 54.6427
COSPr = Qtot VF / Etot | 2.2965
h active | 2440 | hrs/yr
MT heating | J m-2 s-1 | kWh m-2 y-1
E HP | 35.7156 | 87.1461
Epump | 0.34024 | 0.83019
Efans | 4.1761 | 10.1897
Etot | 40.2319 | 98.1659
COSPr = Qtot VF / Etot | 1.2783
h active | 2440 | hrs/yr
Swimming pool heating | J m-2 s-1 | kWh m-2 y-1
E HP | 13.9404 | 81.412
Epump | 0.34024 | 1.987
Efans | 4.1761 | 24.3884
Etot | 18.4568 | 107.7874
COSPr = Qtot VF / Etot | 2.7864
h active | 5840 | hrs/yr

## Int_E2
Integration strategy E2: HP+HP+ATES |  |  |  |  | Integration strategy E2: HP+HP+ATES
HEATING SEASON |  |  |  |  | Non-heating season
HP2 |  |  |  |  | HP2
Condenser |  |  |  |  | Condenser
ε = (Tc,o - Tc,i)/(Th,i - Tc,i) | 90% |  |  |  | ε = (Tc,o - Tc,i)/(Th,i - Tc,i) | 90%
| LT | MT
Tc,i | 0 | 0 | C | Tc,I HE4 | Tc,i | 10 | C | Th,o HE4
Tc,o | 20 | 20 | C | Tc,o HE4 | Tc,o | 30 | C | Th,i HE4
Th,i = Th,o = Tcon = T1 | 22.2222 | 22.2222 | C |  | Th,i = Th,o = Tcon = T1 | 32.2222 | C
Evaporator |  |  |  |  | Evaporator
ε = (Th,i - Th,o) / (Th,i - Tc,i) | 90% |  |  |  | ε = (Th,i - Th,o) / (Th,i - Tc,i) | 90%
| LT | MT
Th,i = Thot in | 31.2 | 31.2 | C |  | Th,i = Thot in | 31.2 | C
Th,o = Thot, out | 17.06 | 17.06 | C |  | Th,o = Thot, out | 17.06 | C
Tc,i = Tc, o | 15.4889 | 15.4889 | C |  | Tc,i = Tc, o | 15.4889 | C
LT heating
Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K) | Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K)
1 - Saturated liquid (100%): subcooling | 22.2222 | 6.1224 | 230.68 |  | 1 - Saturated liquid (100%): subcooling | 32.2222 | 8.3176 | 245.08
2 - liquid + vapour | 15.4889 | 4.9673 | 230.68 |  | 2 - liquid + vapour | 15.4889 | 4.9673 | 245.08
3 - Saturated vapour (100%): superheat | 15.4889 | 4.9673 | 407.55 | 1.7206 | 3 - Saturated vapour (100%): superheat | 15.4889 | 4.9673 | 407.55 | 1.7206
4 -liquid + vapour: highly superheated | 22.941 | 6.1224 | 411.8779 | 1.7206 | 4 -liquid + vapour: highly superheated | 32.9131 | 8.3176 | 417.4063 | 1.7206
MT heating
Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K)
1 - Saturated liquid (100%): subcooling | 22.2222 | 6.1224 | 230.68
2 - liquid + vapour | 15.4889 | 4.9673 | 230.68
3 - Saturated vapour (100%): superheat | 15.4889 | 4.9673 | 407.55 | 1.7206
4 -liquid + vapour: highly superheated | 22.941 | 6.1224 | 411.8779 | 1.7206
Isentropic efficiency E |  |  |  |  | Isentropic efficiency E
E = (h4 - h3) / (h4' - h3) | 70% |  |  |  | E = (h4 - h3) / (h4' - h3) | 70%
h4' | 413.7327 | kJ/kg |  |  | h4' | 421.6304 | kJ/kg
Qcold = Qev | LT | MT |  |  | Qcold = Qev
mw ev | 0.0010206 | 0.0010206 | kg/s |  | mw ev | 0.0010206 | kg/s
Qcold = m * (h3-h2) | -0.060378 | -0.060378 | kJ/s |  | Qcold = m * (h3-h2) | -0.060378 | kJ/s
ṁr = flow rate refrigerant | -0.00034137 | -0.00034137 | kg/s |  | ṁr = flow rate refrigerant | -0.00037163 | kg/s
Cpw | 4184 | 4184 | J/kg K |  | Cpw | 4184 | J/kg K
Qhot = Qcon |  |  |  |  | Qhot = Qcon
Qhot = mr * (h1-h4') | 0.062489 | 0.062489 | kJ/s |  | Qhot = mr * (h1-h4') | 0.065611 | kJ/s
ṁr = flow rate refrigerant | -0.00034137 | -0.00034137 | kg/s |  | ṁr = flow rate refrigerant | -0.00037163 | kg/s
ṁ water through condenser | 0.00074676 | 0.00074676 | kg/s |  | ṁ water through condenser | 0.00078407 | kg/s
COP |  |  |  |  | COP
COPhp = (h4'-h1)/(h4'-h3) | 29.6075 |  |  |  | COPhp = Qcon/Win | 12.5388
Win = Qcon / COPhp | 0.0021106 | kJ/s |  |  | Win = Qcon / COPhp | 0.0052326 | kJ/s
COPref | 28.6075 |  |  |  | COPref | 11.5388
Win = Qev / COPref | 0.0021106 | kJ/s |  |  | Win = Qev / COPref | 0.0052326 | kJ/s
HP3 |  |  |  |  | HP3
Condenser |  |  |  |  | Condenser
ε = (Tc,o - Tc,i)/(Th,i - Tc,i) | 90% |  |  |  | ε = (Tc,o - Tc,i)/(Th,i - Tc,i) | 80% |  | parallel flow, reversible HP cooling modus
| LT | MT
Tc,i | 30 | 50 | C | floor heating/radiator supply temperature | Tc,i | 10 | C | Condenser temperatures HP2
Tc,o | 40 | 70 | C | floor heating/radiator return temperature | Tc,o | 30 | C | Condenser temperatures HP2
Th,i = Th,o = Tcon = T1 | 41.1111 | 72.2222 | C |  | Th,i = Th,o = Tcon = T1 | 35 | C | T1 > T2 (=T3)
Evaporator
ε = (Th,i - Th,o) / (Th,i - Tc,i) | 90% |  |  |  | ε = (Th,i - Th,o) / (Th,i - Tc,i) | 80% |  | parallel flow, reversible HP cooling modus
| LT | MT
Th,i = Thot in | 20 | 20 | C | Condenser temperatures HP2 | Th,i = Thot in | 23 | C | Floor cooling return
Th,o = Thot, out | 0 | 0 | C | Condenser temperatures HP2 | Th,o = Thot, out | 18 | C | Floor cooling supply
Tc,i = Tc, o | -2.2222 | -2.2222 | C |  | Tc,i = Tc, o | 16.75 | C
LT heating
Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K) | Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K)
1 - Saturated liquid (100%): subcooling | 41.1111 | 10.4797 | 258.25 |  | 1 - Saturated liquid (100%): subcooling | 35 | 8.8879 | 249.2
2 - liquid + vapour | -2.2222 | 2.7028 | 258.25 |  | 2 - liquid + vapour | 16.75 | 5.1772 | 249.2
3 - Saturated vapour (100%): superheat | -2.2222 | 2.7028 | 397.48 | 1.7291 | 3 - Saturated vapour (100%): superheat | 16.75 | 5.1772 | 408.28 | 1.7201
4 -liquid + vapour: highly superheated | 41.6888 | 10.4797 | 425.6924 | 1.7291 | 4 -liquid + vapour: highly superheated | 35.0824 | 8.8879 | 418.4873 | 1.7201
MT heating
Phase | T ( C) | P (bar) | H (kJ/kg) | S (kJ/kg K)
1 - Saturated liquid (100%): subcooling | 72.2222 | 22.2351 | 308.66
2 - liquid + vapour | -2.2222 | 2.7028 | 308.66
3 - Saturated vapour (100%): superheat | -2.2222 | 2.7028 | 397.48 | 1.7291
4 -liquid + vapour: highly superheated | 79.9974 | 22.2351 | 441.2246 | 1.7291
Isentropic efficiency E |  |  |  |  | Isentropic efficiency E
E = (h4 - h3) / (h4' - h3) | 70% |  |  |  | E = (h4 - h3) / (h4' - h3) | 70%
| LT | MT
h4' | 437.7834 | 459.9723 | kJ/kg |  | h4' | 422.8618 | kJ/kg
Qcold = Qev | values specific for case study used. See description for calculation method |  |  |  | Qcold = Qev | values specific for case study used. See description for calculation method
Qev HP3 = Qcon HP2 + Qhe 4 |  | kJ/s |  |  | Qcold = m * (h3-h2) |  | kJ/s | cooling demand of the specific host building
Qcond HP2 | 0.062489 | kJ/s |  |  | ṁr = flow rate refrigerant |  | kg/s | using formulae Qcold = m * (h3-h2)
Qhe4 |  | kJ/s | sum of the heat stored in ATES hot source outside heating season by cooling the VF and the specific host-building |  | ṁ water through evaporator |  | kg/s | using formulae Qcold = m *Cpw *dT
Qcold = m * (h3-h2) |  | kJ/s | equal to Qev HP3
ṁr = flow rate refrigerant |  | kg/s | Qcold / (h3-h2), h3 and h2 calculated above
ṁ water through evaporator |  | kg/s | using Qcold = Qev HP3 = m * Cpw *dT
Qhot = Qcon |  |  |  |  | Qhot = Qcon
Qhot = mr * (h1-h4') |  | kJ/s | using mr calculated in Qev |  | Qhot = mr * (h1-h4) |  | kJ/s | flow rate refrigerant calculated in Qev
ṁ water through condenser |  | kg/s | using Qhot = m * Cpw * dT |  | ṁ water through condenser |  | kg/s | using formulae Qhot = m *Cpw *dT
COP cooling | LT | MT |  |  | COP cooling
COPhp = Qcon/Win | 4.4545 | 2.421 |  |  | COPhp = Qcon/Win | 11.9095
Win = Qcon / COPhp |  |  | kJ/s | Using values calculated in Qcon | Win = Qcon / COPhp |  | kJ/s | Using values calculated in Qcon
COPref | 3.4545 | 1.421 |  |  | COPref | 10.9095
Win = Qev / COPref |  |  | kJ/s | Using values calculated in Qev | Win = Qev / COPref |  | kJ/s | Using values calculated in Qev
HE4 |  |  |  |  | HE4
ε = (Tc,o - Tc,i)/(Th,i - Tc,i) | 80% |  |  |  | ε = (Tc,o - Tc,i)/(Th,i - Tc,i) | 80%
ε = (Th,i - Th,o)/(Th,i - Tc,i) | 80% |  |  |  | ε = (Th,i - Th,o)/(Th,i - Tc,i) | 80%
Tc,i | 0 | C |  |  | Tc,i | 5 | C | ATES cold source
Tc,o (water temp to building HP) | 20 | C |  |  | Tc,o (water temp to building HP) | 25 | C | ATES hot source
Th,i | 25 | C | ATES hot source |  | Th,i | 30 | C
Th,o (exhaust air temperature) | 5 | C | ATES cold source |  | Th,o (exhaust air temperature) | 10 | C
values specific for case study used. See description for calculation method
Qhe4 = Qstored |  | kJ/s | Qhe4, calculated in Qev at HP3 |  | Qhe4 = Qstored |  | kJ/s | Sum of Qhot (Qcon) HP3 + Qcon HP2
mw5 = mw3b |  | kg/s | calculated with Qhe4 = mw * CPw * dT |  | mw5 = mw3b |  | kg/s | calculated with Qhe4 = mw * CPw * dT
Energy use pumps |  |  |  |  | Energy use pumps
Energy use pumps within VF system | 0.34024 | J/s |  |  | Energy use pumps within VF system | 0.34024 | J/s
| unit | Pump CON2-EV3 | Pump ATES |  |  | unit | Pump CON2-CON3 | Pump ATES
Head (average) | m | 1 | 100 |  | Head (average) | m | 1 | 100
dP (average pressure difference) | bar | 0.098 | 9.8 |  | dP (average pressure difference) | bar | 0.098 | 9.8
flow rate | kg/s |  |  |  | flow rate | kg/s
Capacity | m3/s |  |  |  | Capacity | m3/s
n pump | % | 72% | 72% |  | n pump | % | 0.72 | 0.72
Epump | kWh |  |  |  | Epump | kWh
p water | 997 | kg/m3 |  |  | p water | 997 | kg/m3
Energy use fans |  |  |  |  | Energy use fans
Energy use fans within VF system | 4.1761 | J/s | VF_CDS: not including the outdoor unit |  | Energy use fans within VF system | 4.1761 | J/s | VF_CDS: not including the outdoor unit
COSP |  |  |  |  | COSP
E HP | J s-1 |  | Energy use by HP1 +HP2+HP3 (HP3 specific per host building) |  | E HP | J s-1 |  | Energy use by HP1 +HP2+HP3 (HP3 specific per host building)
Epump | J s-1 |  | Energy use by pumps within VF system + those for E2 system (specific per host building) |  | Epump | J s-1 |  | Energy use by pumps within VF system + those for E2 system (specific per host building)
Efans | J s-1 | 4.1761 |  |  | Efans | J s-1 | 4.1761
Etot | J s-1 |  | Ehp + Efan + Epumps |  | Etot | J s-1 |  | Ehp + Efan + Epumps
COSPr |  |  | Qtot VF / Etot |  | COSPr |  |  | Qtot VF / Etot

## BS_Ap
Baseline energy use of an 80m2 apartment
|  | BENG | A-label | C-label
HEATING
Heat demands | kWh y | 3269.3094 | 4441.5662 | 6051.634 | Appendix C.1
Heat demands | kJ/s | 0.89325 | 1.2135 | 1.6535 | Appendix C.1
Supply temp heat system | C | 40 | 40 | 70 | Appendix C.2
Return temp heat system | C | 30 | 30 | 50 | Appendix C.2
Av. Ambient temperature | C | 4.5 | 4.5 | 4.5 | Appendix C.2
Heating hours | h y-1 | 3660 | 3660 | 3660 | Appendix C.2
COP heating | - | 4.3702 | 4.3702 | 2.3938
Win HP | kWh y-1 | 748.0935 | 1016.3329 | 2528.0028
mr (refrigerant flowrate) | kg/s | 0.0049647 | 0.0067449 | 0.010898
Qcold | kJ/s | 0.68886 | 0.93586 | 0.96274
Vair | kg/s | 0.10155 | 0.13796 | 0.14192
Vair | m3/s | 0.082894 | 0.11262 | 0.11585
Pressure difference | Pa | 103.3031 | 103.3031 | 103.3031
Efans | kW | 0.013174 | 0.017898 | 0.018412
Efans | kWh | 48.2174 | 65.5065 | 67.3883
Etotal heating | kWh y-1 | 796.3109 | 1081.8394 | 2595.3911
Etotal heating | kWh m-2 y-1 | 9.9539 | 13.523 | 32.4424
COOLING
Cooling demands | kWh y-1 | 200 | 200 | 360 | Appendix C.1
Cooling demands | kJ/s | 0.75472 | 0.75472 | 1.3585 | Appendix C.1
Supply temp cooling system | C | 18 | 18 | 18 | Appendix C.2
Return temp cooling system | C | 23 | 23 | 23 | Appendix C.2
Av. Ambient temp | C | 26.4 | 26.4 | 26.4 | Appendix C.2
Cooling hours | h y-1 | 265 | 265 | 265 | Appendix C.2
COP cooling | - | 8.8608 | 8.8608 | 8.8608
Win HP | kWh y-1 | 22.5714 | 22.5714 | 40.6285
mr (refrigerant flowrate) | kg/s | 0.0048324 | 0.0048324 | 0.0086982
Qhot | kJ/s | 0.83989 | 0.83989 | 1.5118
Vair | kg/s | 0.097973 | 0.097973 | 0.17635
Vair | m3/s | 0.079978 | 0.079978 | 0.14396
Pressure difference | Pa | 103.3031 | 103.3031 | 103.3031
Efans | kW | 0.012711 | 0.012711 | 0.022879
Efans | kWh | 3.3684 | 3.3684 | 6.063
Etotal cooling | kWh y-1 | 25.9398 | 25.9398 | 46.6916
Etotal cooling | kWh m-2 y-1 | 0.32425 | 0.32425 | 0.58364
YEAR-ROUND
Etotal heating + cooling | kWh y-1 | 822.2507 | 1107.7792 | 2642.0827
Etotal heating + cooling | kWh m-2 y-1 | 10.2781 | 13.8472 | 33.026

## BS_off
Baseline energy use of an office
|  | SMALL OFFICE |  |  | LARGE OFFICE
|  | BENG | A-label | C-label | BENG | A-label | C-label
HEATING
Heat demands | kWh m-2 y-1 | 22.8 | 95.3175 | 108.5062 | 34.3 | 68.94 | 86.525 | Appendix C.1
Heat demands | kJ/s | 0.0062295 | 0.026043 | 0.029647 | 0.0093716 | 0.018836 | 0.023641 | Appendix C.1
Supply temp heat system | C | 40 | 40 | 70 | 40 | 40 | 70 | Appendix C.2
Return temp heat system | C | 30 | 30 | 50 | 30 | 30 | 50 | Appendix C.2
Av. Ambient temperature | C | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | Appendix C.2
Heating hours | h y-1 | 3660 | 3660 | 3660 | 3660 | 3660 | 3660 | Appendix C.2
COP heating | - | 4.3702 | 4.3702 | 2.3938 | 4.3702 | 4.3702 | 2.3938
Win HP | kWh m-2 y-1 | 5.2172 | 21.8108 | 45.3273 | 7.8486 | 15.7751 | 36.1449
mr (refrigerant flowrate) | kg/s | 3.4624e-05 | 0.00014475 | 0.0001954 | 5.2088e-05 | 0.00010469 | 0.00015582
Qcold | kJ/s | 0.0048041 | 0.020084 | 0.017262 | 0.0072271 | 0.014526 | 0.013765
Vair | kg/s | 0.00070817 | 0.0029606 | 0.0025446 | 0.0010654 | 0.0021413 | 0.0020291
Vair | m3/s | 0.0005781 | 0.0024168 | 0.0020772 | 0.00086968 | 0.001748 | 0.0016564
Pressure difference | Pa | 103.3031 | 103.3031 | 103.3031 | 103.3031 | 103.3031 | 103.3031
Efans | kW | 9.1876e-05 | 0.0003841 | 0.00033013 | 0.00013822 | 0.0002778 | 0.00026325
Efans | kWh m-2 y-1 | 0.33627 | 1.4058 | 1.2083 | 0.50587 | 1.0168 | 0.9635
Etotal heating | kWh m-2 y-1 | 5.5534 | 23.2166 | 46.5356 | 8.3545 | 16.7918 | 37.1084
COOLING
Cooling demands | kWh m-2 y-1 | 11.4 | 51 | 48.28 | 17.2 | 59.16 | 57.12 | Appendix C.1
Cooling demands | kJ/s | 0.0026419 | 0.011819 | 0.011189 | 0.0039861 | 0.01371 | 0.013238 | Appendix C.1
Supply temp cooling system | C | 18 | 18 | 18 | 18 | 18 | 18 | Appendix C.2
Return temp cooling system | C | 23 | 23 | 23 | 23 | 23 | 23 | Appendix C.2
Av. Ambient temp | C | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | Appendix C.2
Cooling hours | h y-1 | 4315 | 4315 | 4315 | 4315 | 4315 | 4315 | Appendix C.2
COP cooling | - | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583 | 18.9583
Win HP | kWh m-2 y-1 | 0.60132 | 2.6901 | 2.5466 | 0.90725 | 3.1205 | 3.0129
mr (refrigerant flowrate) | kg/s | 1.5445e-05 | 6.9094e-05 | 6.5409e-05 | 2.3302e-05 | 8.0149e-05 | 7.7385e-05
Qhot | kJ/s | 0.0027813 | 0.012443 | 0.011779 | 0.0041964 | 0.014433 | 0.013936
Vair | kg/s | 0.00037653 | 0.0016845 | 0.0015946 | 0.00056809 | 0.001954 | 0.0018866
Vair | m3/s | 0.00030737 | 0.0013751 | 0.0013017 | 0.00046375 | 0.0015951 | 0.0015401
Pressure differene | Pa | 103.3031 | 103.3031 | 103.3031 | 103.3031 | 103.3031 | 103.3031
Efans | kW | 4.8849e-05 | 0.00021854 | 0.00020688 | 7.3703e-05 | 0.0002535 | 0.00024476
Efans | kWh m-2 y-1 | 0.21078 | 0.94299 | 0.89269 | 0.31803 | 1.0939 | 1.0561
Etotal cooling | kWh m-2 y-1 | 0.8121 | 3.6331 | 3.4393 | 1.2253 | 4.2144 | 4.0691
YEAR-ROUND
Etotal heating + cooling | kWh m-2 y-1 | 6.3655 | 26.8497 | 49.9749 | 9.5798 | 21.0062 | 41.1774

## BS_res
Baseline energy use of a 250m2 restaurant
HEATING
Heat demands | kWh y | 47966.6019 | Appendix C.1
Heat demands | kJ/s | 13.1056 | Appendix C.1
Supply temp heat system | C | 40 | Appendix C.2
Return temp heat system | C | 30 | Appendix C.2
Av. Ambient temperature | C | 4.5 | Appendix C.2
Heating hours | h y-1 | 3660 | Appendix C.2
COP heating | -
Win HP | kWh y-1 | 4.4
mr (refrigerant flowrate) | kg/s | 0.072842
Qcold | kJ/s | 10.107
Vair | kg/s | 1.4789
Vair | m3/s | 1.2073
Pressure difference | Pa | 103.3031
Efans | kW | 0.19187
Efans | kWh | 702.2342
Etotal heating | kWh y-1 | 11678.1006
Etotal heating | kWh m-2 y-1 | 46.7124
COOLING
Cooling demands | kWh y-1 | 14662.6531 | Appendix C.1
Cooling demands | kJ/s | 2.875 | Appendix C.1
Supply temp cooling system | C | 18 | Appendix C.2
Return temp cooling system | C | 23 | Appendix C.2
Av. Ambient temp | C | 24.7 | Appendix C.2
COP cooling | - | 9.9 | Appendix C.2
Win HP | kWh y-1 | 1484.6927
mr (refrigerant flowrate) | kg/s | 0.018089
Qhot | kJ/s | 3.1661
Vair | kg/s | 0.37957
Vair | m3/s | 0.30985
Pressure difference | Pa | 103.3031
Efans | kW | 0.049244
Efans | kWh | 251.143
Etotal cooling | kWh y-1 | 1735.8357
Etotal cooling | kWh m-2 y-1 | 6.9433
YEAR-ROUND
Etotal heating + cooling | kWh y-1 | 13413.9362
Etotal heating + cooling | kWh m-2 y-1 | 53.6557

## BS_Sw
Baseline energy use of a swimming pool (1m2 water surface)
|  | Indoor | Outdoor
HEATING
Heat demands | kWh y | 2022.275 | 141.5593 | Appendix C.1
Heat demands | kJ/s | 0.55435 | 0.094373 | Appendix C.1
Supply temp heat system | C | 30 | 30 | Appendix C.2
Return temp heat system | C | 23 | 23 | Appendix C.2
Av. Ambient temperature | C | 11 | 16 | Appendix C.2
Heating hours | h y-1 | 3648 | 1 | Appendix C.2
COP heating | - | 4.8 | 5.5
Win HP | kWh y-1 | 419.1752 | 25.553
mr (refrigerant flowrate) | kg/s | 0.0029199 | 0.00050416
Qcold | kJ/s | 0.43945 | 0.077337
Vair | kg/s | 0.024292 | 0.0032222
Vair | m3/s | 0.01983 | 0.0026304
Pressure difference | Pa | 103.3031 | 103.3031
Efans | kW | 0.0031516 | 0.00041804
Efans | kWh | 11.497 | 0.62706
Etotal heating | kWh y-1 | 430.6722 | 26.1801
Etotal heating | kWh m-2 y-1 | 430.6722 | 26.1801
YEAR-ROUND
Etotal heating + cooling | kWh y-1 | 430.6722 | 26.1801
Etotal heating + cooling | kWh m-2 y-1 | 430.6722 | 26.1801