## ESOLinput (June to August)
Setup to calculate daily average solar irradiance at different orientations of the solar collection system considering all summer season of Madrid
Item | Description/Inputs
Assessment Tool | System Advisor Model | SAM 2023.12.17
Location | Madrid, Spain | Weather Data Download - Madrid 082210 (IWEC)
Array Type | Fixed Roof Mount
Tilt Angels | 90°
60°
30°
0°
Azimuth Angel | North (N) | 0o
| South (S) | 180o
| East (E) | 90o
| West (W) | 270o
Months of Madrid Whole Summer Design Period | All summer season: June to August
A tile angel of 90o
Façade feature |  | Vertical Façade
Orientation of the Opaque Façade |  | North (N) | South (S) | East (E) | West (W)
Azimuth Angel |  | 0o | 180o | 90o | 270o
Plane array irradiance (kWh/m2/month) | Jun | 57.6594 | 84.0516 | 112.86 | 107.732
| Jul | 55.1956 | 95.8231 | 120.925 | 115.604
| Aug | 46.6749 | 111.062 | 109.671 | 104.071
A tile angel of 60o
Façade feature |  | Vertical Façade/overhang
Orientation of the Opaque Façade |  | North (N) | South (S) | East (E) | West (W)
Azimuth Angel |  | 0o | 180o | 90o | 270o
Plane array irradiance (kWh/m2/month) | Jun | 111.075 | 158.317 | 159.604 | 152.622
| Jul | 106.493 | 178.273 | 170.715 | 164.227
| Aug | 67.9425 | 179.562 | 151.372 | 144.066
A tile angel of 30o
Façade feature |  | Overhang
Orientation of the Overhang |  | North (N) | South (S) | East (E) | West (W)
Azimuth Angel |  | 0o | 180o | 90o | 270o
Plane array irradiance (kWh/m2/month) | Jun | 180.905 | 207.368 | 198.943 | 193.7
| Jul | 187.807 | 228.445 | 213.554 | 208.367
| Aug | 147.067 | 211.454 | 184.613 | 179.788
A tile angel of 0o
Façade feature |  | Overhang
Orientation of the Overhang |  | North (N) | South (S) | East (E) | West (W)
Azimuth Angel |  | 0o | 180o | 90o | 270o
Plane array irradiance (kWh/m2/month) | Jun | 214.09 | 214.09 | 214.09 | 214.09
| Jul | 229.91 | 229.91 | 229.91 | 229.91
| Aug | 197.431 | 197.431 | 197.431 | 197.431
Surface tile angel of 90° | Plane array irradiance (kWh/m2/month)
| Month | North (N) | South (S) | East (E) | West (W)
| Jun | 57.6594 | 84.0516 | 112.86 | 107.732
| Jul | 55.1956 | 95.8231 | 120.925 | 115.604
| Aug | 46.6749 | 111.062 | 109.671 | 104.071
Surface tile angel of 60° | Plane array irradiance (kWh/m2/month)
| Month | North (N) | South (S) | East (E) | West (W)
| Jun | 111.075 | 158.317 | 159.604 | 152.622
| Jul | 106.493 | 178.273 | 170.715 | 164.227
| Aug | 67.9425 | 179.562 | 151.372 | 144.066
Surface tile angel of 30° | Plane array irradiance (kWh/m2/month)
| Month | North (N) | South (S) | East (E) | West (W)
| Jun | 180.905 | 207.368 | 198.943 | 193.7
| Jul | 187.807 | 228.445 | 213.554 | 208.367
| Aug | 147.067 | 211.454 | 184.613 | 179.788
Surface tile angel of 0° | Plane array irradiance (kWh/m2/month)
| Month | North (N) | South (S) | East (E) | West (W)
| Jun | 214.09 | 214.09 | 214.09 | 214.09
| Jul | 229.91 | 229.91 | 229.91 | 229.91
| Aug | 197.431 | 197.431 | 197.431 | 197.431
| Tilt Angel | Summer season plane array irradiance (ESOLinput) (kWh/m2/summer season) considering Orientation of the solar collection system
|  | North (N) | South (S) | East (E) | West (W)
| Surface tile angel of 90° | 159.5299 | 290.9367 | 343.456 | 327.407
| Surface tile angel of 60° | 285.5105 | 516.152 | 481.691 | 460.915
| Surface tile angel of 30° | 515.779 | 647.267 | 597.11 | 581.855
| Surface tile angel of 0° | 641.431 | 641.431 | 641.431 | 641.431

## ESCOOLout
Note: Cells highlighted in yellow are the ones having solar fraction 1 or more (including losses)
Envelop Possibilities | Scenarios per configuration | Design features |  |  | Orientation of the Building Main Entrance to the North
[5 empty] | Sureface Tilt angels | Area for collection Devcies Per Façade Orientation (STC/PV) | [7 empty] | Thermally-Driven |  |  |  | Electrically-driven
[6 empty] | N |  | S |  | E |  | W |  | Double-effect chillers with evacuated tubes collectors |  |  |  | Water-cooled vapor compression chiller and Polycrystalline PV panel
[6 empty] | SOLarry (N) (m2) | (ESOLinput) (N) (kWh/m2/summer season) | SOLarry (S) (m2) | (ESOLinput) (S) (kWh/m2/summer season) | SOLarry (E) (m2) | (ESOLinput) (E) (kWh/m2/summer season) | SOLarry (W) (m2) | (ESOLinput) (E) (kWh/m2/summer season) | COPcoolsys | COPsolarsys | ESCOOLout (kWh/summer season)(excluding losses) | ESCOOLout (kWh/summer season) (including losses) | COPcoolsys | COPsolarsys | ESCOOLout (kWh/summer season)(excluding losses) | ESCOOLout (kWh/summer season) (including losses)
Roofs Tops | Installing solar collection devices on rooftops | On the top of flat roofs with a particular tilt angel and orientation | Option one: Use Factor of 0,15 |  | 30 | 0 | 515.779 | 427.68 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | 215922.0574 | 185692.9694 | 2.6 | 0.22 | 158342.8421 | 136174.8442
|  |  | Option two: Use Factor of 0,25 |  | 30 | 0 | 515.779 | 712.8 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | 359870.0957 | 309488.2823 | 2.6 | 0.22 | 263904.7369 | 226958.0737
|  |  | Option three: Use Factor of 0,40 |  | 30 | 0 | 515.779 | 1140.48 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | 575792.1532 | 495181.2517 | 2.6 | 0.22 | 422247.579 | 363132.9179
|  |  | Option four: Use Factor of 0,50 |  | 30 | 0 | 515.779 | 1425.6 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | 719740.1915 | 618976.5647 | 2.6 | 0.22 | 527809.4737 | 453916.1474
|  |  | Option five: Use Factor of 0,6 |  | 30 | 0 | 515.779 | 1710.72 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | 863688.2297 | 742771.8776 | 2.6 | 0.22 | 633371.3685 | 544699.3769
Flat Roofs & Façade | Installing solar collection devices on rooftops and considering vertical attachment of solar collection devices along the external layer of the opaque façades | Vertical Façade along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  |  | 90 | 0 | 159.5299 | 1670 | 290.9367 | 0 | 343.456 | 0 | 327.407 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  | On the top of flat roofs with a particular tilt angel and orientation | Option one: Use Factor of 0,15 |  | 30 | 0 | 515.779 | 427.68 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | 594896.2029 | 511610.7345 | 2.6 | 0.22 | 436257.2154 | 375181.2053
|  |  | Option two: Use Factor of 0,25 |  | 30 | 0 | 515.779 | 712.8 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | 738844.2411 | 635406.0474 | 2.6 | 0.22 | 541819.1102 | 465964.4348
|  |  | Option three: Use Factor of 0,40 |  | 30 | 0 | 515.779 | 1140.48 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | 954766.2986 | 821099.0168 | 2.6 | 0.22 | 700161.9523 | 602139.279
|  |  | Option four: Use Factor of 0,50 |  | 30 | 0 | 515.779 | 1425.6 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | 1098714.3369 | 944894.3297 | 2.6 | 0.22 | 805723.847 | 692922.5085
|  |  | Option five: Use Factor of 0,6 |  | 30 | 0 | 515.779 | 1710.72 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | 1242662.3752 | 1068689.6426 | 2.6 | 0.22 | 911285.7418 | 783705.7379
| Installing solar collection devices on rooftops and considering vertical attachment of solar collection devices along the external layer of the opaque façades and additional overhangs for installing the collector at different tilt angles | Vertical Façade along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  |  | 90 | 0 | 159.5299 | 1670 | 290.9367 | 0 | 343.456 | 0 | 327.407 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  | Rooftop and overhang features | Option 1 | Rooftop: Use Factor of 0,15 | 30 | 0 | 515.779 | 427.68 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 285.5105 | 10.5 | 516.152 | 5.25 | 481.691 | 5.25 | 460.915 | 1.2 | 0.65 | 602983.4593 | 518565.775 | 2.6 | 0.22 | 442187.8702 | 380281.5683
|  |  | Option 2 | Rooftop: Use Factor of 0,15 | 30 | 0 | 515.779 | 427.68 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 515.779 | 10.5 | 647.267 | 5.25 | 597.11 | 5.25 | 581.855 | 1.2 | 0.65 | 605025.1813 | 520321.6559 | 2.6 | 0.22 | 443685.1329 | 381569.2143
|  |  | Option 3 | Rooftop: Use Factor of 0,15 | 30 | 0 | 515.779 | 427.68 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 641.431 | 10.5 | 641.431 | 5.25 | 641.431 | 5.25 | 641.431 | 1.2 | 0.65 | 605402.8426 | 520646.4447 | 2.6 | 0.22 | 443962.0846 | 381807.3928
|  |  | Option 4 | Rooftop: Use Factor of 0,25 | 30 | 0 | 515.779 | 712.8 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 285.5105 | 10.5 | 516.152 | 5.25 | 481.691 | 5.25 | 460.915 | 1.2 | 0.65 | 746931.4976 | 642361.0879 | 2.6 | 0.22 | 547749.7649 | 471064.7978
|  |  | Option 5 | Rooftop: Use Factor of 0,25 | 30 | 0 | 515.779 | 712.8 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 515.779 | 10.5 | 647.267 | 5.25 | 597.11 | 5.25 | 581.855 | 1.2 | 0.65 | 748973.2196 | 644116.9688 | 2.6 | 0.22 | 549247.0277 | 472352.4438
|  |  | Option 6 | Rooftop: Use Factor of 0,25 | 30 | 0 | 515.779 | 712.8 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 641.431 | 10.5 | 641.431 | 5.25 | 641.431 | 5.25 | 641.431 | 1.2 | 0.65 | 749350.8809 | 644441.7576 | 2.6 | 0.22 | 549523.9793 | 472590.6222
|  |  | Option 7 | Rooftop: Use Factor of 0,40 | 30 | 0 | 515.779 | 1140.48 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 285.5105 | 10.5 | 516.152 | 5.25 | 481.691 | 5.25 | 460.915 | 1.2 | 0.65 | 962853.555 | 828054.0573 | 2.6 | 0.22 | 706092.607 | 607239.642
|  |  | Option 8 | Rooftop: Use Factor of 0,40 | 30 | 0 | 515.779 | 1140.48 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 515.779 | 10.5 | 647.267 | 5.25 | 597.11 | 5.25 | 581.855 | 1.2 | 0.65 | 964895.277 | 829809.9382 | 2.6 | 0.22 | 707589.8698 | 608527.288
|  |  | Option 9 | Rooftop: Use Factor of 0,40 | 30 | 0 | 515.779 | 1140.48 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 641.431 | 10.5 | 641.431 | 5.25 | 641.431 | 5.25 | 641.431 | 1.2 | 0.65 | 965272.9384 | 830134.727 | 2.6 | 0.22 | 707866.8215 | 608765.4665
|  |  | Option 10 | Rooftop: Use Factor of 0,5 | 30 | 0 | 515.779 | 1425.6 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 285.5105 | 10.5 | 516.152 | 5.25 | 481.691 | 5.25 | 460.915 | 1.2 | 0.65 | 1106801.5933 | 951849.3703 | 2.6 | 0.22 | 811654.5018 | 698022.8715
|  |  | Option 11 | Rooftop: Use Factor of 0,5 | 30 | 0 | 515.779 | 1425.6 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 515.779 | 10.5 | 647.267 | 5.25 | 597.11 | 5.25 | 581.855 | 1.2 | 0.65 | 1108843.3153 | 953605.2511 | 2.6 | 0.22 | 813151.7645 | 699310.5175
|  |  | Option 12 | Rooftop: Use Factor of 0,5 | 30 | 0 | 515.779 | 1425.6 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 641.431 | 10.5 | 641.431 | 5.25 | 641.431 | 5.25 | 641.431 | 1.2 | 0.65 | 1109220.9767 | 953930.0399 | 2.6 | 0.22 | 813428.7162 | 699548.6959
|  |  | Option 13 | Rooftop: Use Factor of 0,6 | 30 | 0 | 515.779 | 1710.72 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 285.5105 | 10.5 | 516.152 | 5.25 | 481.691 | 5.25 | 460.915 | 1.2 | 0.65 | 1250749.6316 | 1075644.6832 | 2.6 | 0.22 | 917216.3965 | 788806.101
|  |  | Option 14 | Rooftop: Use Factor of 0,6 | 30 | 0 | 515.779 | 1710.72 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 515.779 | 10.5 | 647.267 | 5.25 | 597.11 | 5.25 | 581.855 | 1.2 | 0.65 | 1252791.3536 | 1077400.5641 | 2.6 | 0.22 | 918713.6593 | 790093.747
|  |  | Option 15 | Rooftop: Use Factor of 0,6 | 30 | 0 | 515.779 | 1710.72 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 00) | 0 | 0 | 641.431 | 10.5 | 641.431 | 5.25 | 641.431 | 5.25 | 641.431 | 1.2 | 0.65 | 1253169.0149 | 1077725.3529 | 2.6 | 0.22 | 918990.611 | 790331.9254
| Installing solar collection devices on rooftops and considering vertical attachment of solar collection devices along the external layer of the opaque façades and parapets of balconies and roofs and also additional overhangs for installing the collector at different tilt angles | Vertical Façade | Along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  | 90 | 0 | 159.5299 | 1670 | 290.9367 | 0 | 343.456 | 0 | 327.407 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  | Along parapets of balconies and roofs |  | 90 | 110.88 | 159.5299 | 63.36 | 290.9367 | 269.28 | 343.456 | 269.28 | 327.407 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  | Rooftop and overhang features | Option 1 | Rooftop: Use Factor of 0,15 | 30 | 0 | 515.779 | 427.68 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 285.5105 | 10.5 | 516.152 | 5.25 | 481.691 | 5.25 | 460.915 | 1.2 | 0.65 | 772065.9417 | 663976.7098 | 2.6 | 0.22 | 566181.6905 | 486916.2539
|  |  | Option 2 | Rooftop: Use Factor of 0,15 | 30 | 0 | 515.779 | 427.68 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 515.779 | 10.5 | 647.267 | 5.25 | 597.11 | 5.25 | 581.855 | 1.2 | 0.65 | 774107.6636 | 665732.5907 | 2.6 | 0.22 | 567678.9533 | 488203.8998
|  |  | Option 3 | Rooftop: Use Factor of 0,15 | 30 | 0 | 515.779 | 427.68 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 641.431 | 10.5 | 641.431 | 5.25 | 641.431 | 5.25 | 641.431 | 1.2 | 0.65 | 774485.325 | 666057.3795 | 2.6 | 0.22 | 567955.905 | 488442.0783
|  |  | Option 4 | Rooftop: Use Factor of 0,25 | 30 | 0 | 515.779 | 712.8 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 285.5105 | 10.5 | 516.152 | 5.25 | 481.691 | 5.25 | 460.915 | 1.2 | 0.65 | 916013.9799 | 787772.0228 | 2.6 | 0.22 | 671743.5853 | 577699.4834
|  |  | Option 5 | Rooftop: Use Factor of 0,25 | 30 | 0 | 515.779 | 712.8 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 515.779 | 10.5 | 647.267 | 5.25 | 597.11 | 5.25 | 581.855 | 1.2 | 0.65 | 918055.7019 | 789527.9036 | 2.6 | 0.22 | 673240.8481 | 578987.1293
|  |  | Option 6 | Rooftop: Use Factor of 0,25 | 30 | 0 | 515.779 | 712.8 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 641.431 | 10.5 | 641.431 | 5.25 | 641.431 | 5.25 | 641.431 | 1.2 | 0.65 | 918433.3633 | 789852.6924 | 2.6 | 0.22 | 673517.7997 | 579225.3078
|  |  | Option 7 | Rooftop: Use Factor of 0,40 | 30 | 0 | 515.779 | 1140.48 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 285.5105 | 10.5 | 516.152 | 5.25 | 481.691 | 5.25 | 460.915 | 1.2 | 0.65 | 1131936.0374 | 973464.9921 | 2.6 | 0.22 | 830086.4274 | 713874.3276
|  |  | Option 8 | Rooftop: Use Factor of 0,40 | 30 | 0 | 515.779 | 1140.48 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 515.779 | 10.5 | 647.267 | 5.25 | 597.11 | 5.25 | 581.855 | 1.2 | 0.65 | 1133977.7593 | 975220.873 | 2.6 | 0.22 | 831583.6902 | 715161.9736
|  |  | Option 9 | Rooftop: Use Factor of 0,40 | 30 | 0 | 515.779 | 1140.48 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 641.431 | 10.5 | 641.431 | 5.25 | 641.431 | 5.25 | 641.431 | 1.2 | 0.65 | 1134355.4207 | 975545.6618 | 2.6 | 0.22 | 831860.6419 | 715400.152
|  |  | Option 10 | Rooftop: Use Factor of 0,5 | 30 | 0 | 515.779 | 1425.6 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 285.5105 | 10.5 | 516.152 | 5.25 | 481.691 | 5.25 | 460.915 | 1.2 | 0.65 | 1275884.0757 | 1097260.3051 | 2.6 | 0.22 | 935648.3222 | 804657.5571
|  |  | Option 11 | Rooftop: Use Factor of 0,5 | 30 | 0 | 515.779 | 1425.6 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 515.779 | 10.5 | 647.267 | 5.25 | 597.11 | 5.25 | 581.855 | 1.2 | 0.65 | 1277925.7976 | 1099016.186 | 2.6 | 0.22 | 937145.5849 | 805945.203
|  |  | Option 12 | Rooftop: Use Factor of 0,5 | 30 | 0 | 515.779 | 1425.6 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 641.431 | 10.5 | 641.431 | 5.25 | 641.431 | 5.25 | 641.431 | 1.2 | 0.65 | 1278303.459 | 1099340.9747 | 2.6 | 0.22 | 937422.5366 | 806183.3815
|  |  | Option 13 | Rooftop: Use Factor of 0,6 | 30 | 0 | 515.779 | 1710.72 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 285.5105 | 10.5 | 516.152 | 5.25 | 481.691 | 5.25 | 460.915 | 1.2 | 0.65 | 1419832.114 | 1221055.618 | 2.6 | 0.22 | 1041210.2169 | 895440.7865
|  |  | Option 14 | Rooftop: Use Factor of 0,6 | 30 | 0 | 515.779 | 1710.72 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 515.779 | 10.5 | 647.267 | 5.25 | 597.11 | 5.25 | 581.855 | 1.2 | 0.65 | 1421873.8359 | 1222811.4989 | 2.6 | 0.22 | 1042707.4797 | 896728.4325
|  |  | Option 15 | Rooftop: Use Factor of 0,6 | 30 | 0 | 515.779 | 1710.72 | 647.267 | 0 | 597.11 | 0 | 581.855 | 1.2 | 0.65 | - | - | 2.6 | 0.22 | - | -
|  |  |  | Overhang (tilt angel of 00) | 0 | 0 | 641.431 | 10.5 | 641.431 | 5.25 | 641.431 | 5.25 | 641.431 | 1.2 | 0.65 | 1422251.4973 | 1223136.2877 | 2.6 | 0.22 | 1042984.4313 | 896966.611

## Costs-Solar Collection Devices
Note: Cells highlighted in yellow are the ones having solar fraction 1 or more (including losses)
Envelop Possibilities | Scenarios per configuration | Design features |  |  | Orientation of the Building Main Entrance to the North
[5 empty] | Sureface Tilt angels | Area for collection Devcies Per Façade Orientation (STC/PV) |  |  |  | Thermally-Driven | [9 empty] | Electrically-driven
[6 empty] | N | S | E | W | Double-effect chillers with evacuated tubes collectors | [9 empty] | Water-cooled vapor compression chiller and Polycrystalline PV panel
[6 empty] | SOLarry (N) (m2) | SOLarry (S) (m2) | SOLarry (E) (m2) | SOLarry (W) (m2) | Total Area of Solar Collection Devices (m2) | Specific cost of collectors [€/m2] | Specific cost of collectors collector auxiliaries [€/m2] | Total Investment cost of collectors [€] | O&M cost of collectors [€] | O&M cost of collectors auxiliaries [€] | Total O&M cost of collectors [€] | Total annualized investment cost of collectors [€/year] | Total annualized O&M cost of collectors [€/year] | Total annualized investment and O&M cost of collectors [€/year] | Total Area of Solar Collection Devices (m2) | Specific cost of PV panels [€/m2] | Investment cost of PV panels [€] | Specific cost of solar mounting system [€/m2] | Investment cost of solar mounting system [€] | Total Investment cost of PV panels and solar mounting system [€] | O&M cost of PV panels and solar mounting system [€] | Total annualized investment cost of PV panels and solar mounting system[€/year] | Total annualized O&M cost of PV panels [€/year] | Total annualized investment and O&M cost of PV panels and solar mounting system [€/year]
Roofs Tops | Installing solar collection devices on rooftops | On the top of flat roofs with a particular tilt angel and orientation | Option one: Use Factor of 0,15 |  | 30 | 0 | 427.68 | 0 | 0 | 427.68 | 335.6986 | 81.1155 | 178263.0667 | 2153.5738 | 867.287 | 3020.8608 | 15541.7865 | 263.3724 | 15805.1589 | 427.68 | 88 | 37635.84 | 9.64 | 4122.8352 | 41758.6752 | 417.5868 | 3640.7116 | 36.4071 | 3677.1187
|  |  | Option two: Use Factor of 0,25 |  | 30 | 0 | 712.8 | 0 | 0 | 712.8 | 313.3286 | 56.8456 | 263860.1662 | 3350.1089 | 1012.9893 | 4363.0982 | 23004.5317 | 380.3948 | 23384.9265 | 712.8 | 88 | 62726.4 | 9.64 | 6871.392 | 69597.792 | 695.9779 | 6067.8527 | 60.6785 | 6128.5312
|  |  | Option three: Use Factor of 0,40 |  | 30 | 0 | 1140.48 | 0 | 0 | 1140.48 | 294.0653 | 40.9854 | 382118.6712 | 5030.6338 | 1168.577 | 6199.2109 | 33314.8471 | 540.4755 | 33855.3225 | 1140.48 | 88 | 100362.24 | 9.64 | 10994.2272 | 111356.4672 | 1113.5647 | 9708.5643 | 97.0856 | 9805.6499
|  |  | Option four: Use Factor of 0,50 |  | 30 | 0 | 1425.6 | 0 | 0 | 1425.6 | 285.3389 | 35.0898 | 456803.0309 | 6101.6862 | 1250.5988 | 7352.285 | 39826.1699 | 641.0057 | 40467.1756 | 1425.6 | 88 | 125452.8 | 9.64 | 13742.784 | 139195.584 | 1391.9558 | 12135.7053 | 121.3571 | 12257.0624
|  |  | Option five: Use Factor of 0,6 |  | 30 | 0 | 1710.72 | 0 | 0 | 1710.72 | 278.4014 | 30.9079 | 529141.7295 | 7144.0033 | 1321.8711 | 8465.8744 | 46132.9873 | 738.0935 | 46871.0808 | 1710.72 | 88 | 150543.36 | 9.64 | 16491.3408 | 167034.7008 | 1670.347 | 14562.8464 | 145.6285 | 14708.4749
Flat Roofs & Façade | Installing solar collection devices on rooftops and considering vertical attachment of solar collection devices along the external layer of the opaque façades | Vertical Façade along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  |  | 90 | 0 | 1670 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | On the top of flat roofs with a particular tilt angel and orientation | Option one: Use Factor of 0,15 |  | 30 | 0 | 427.68 | 0 | 0 | 2097.68 | 270.8419 | 26.8184 | 624395.9202 | 8522.0938 | 1406.4083 | 9928.5021 | 54437.6817 | 865.6121 | 55303.2937 | 2097.68 | 88 | 184595.84 | 9.64 | 20221.6352 | 204817.4752 | 2048.1748 | 17856.9208 | 178.5692 | 18035.49
|  |  | Option two: Use Factor of 0,25 |  | 30 | 0 | 712.8 | 0 | 0 | 2382.8 | 266.2219 | 24.542 | 692832.2017 | 9515.3033 | 1461.9662 | 10977.2695 | 60404.2686 | 957.0484 | 61361.3169 | 2382.8 | 88 | 209686.4 | 9.64 | 22970.192 | 232656.592 | 2326.5659 | 20284.0619 | 202.8406 | 20486.9025
|  |  | Option three: Use Factor of 0,40 |  | 30 | 0 | 1140.48 | 0 | 0 | 2810.48 | 260.3546 | 21.8782 | 793209.6025 | 10975.8207 | 1537.2056 | 12513.0263 | 69155.6278 | 1090.9427 | 70246.5704 | 2810.48 | 88 | 247322.24 | 9.64 | 27093.0272 | 274415.2672 | 2744.1527 | 23924.7735 | 239.2477 | 24164.0212
|  |  | Option four: Use Factor of 0,50 |  | 30 | 0 | 1425.6 | 0 | 0 | 3095.6 | 256.9804 | 20.4552 | 858829.8287 | 11932.6295 | 1583.0299 | 13515.6594 | 74876.6981 | 1178.3568 | 76055.0549 | 3095.6 | 88 | 272412.8 | 9.64 | 29841.584 | 302254.384 | 3022.5438 | 26351.9146 | 263.5191 | 26615.4337
|  |  | Option five: Use Factor of 0,6 |  | 30 | 0 | 1710.72 | 0 | 0 | 3380.72 | 253.9419 | 19.2385 | 923546.6112 | 12877.597 | 1626.0036 | 14503.6006 | 80519.0021 | 1264.49 | 81783.4921 | 3380.72 | 88 | 297503.36 | 9.64 | 32590.1408 | 330093.5008 | 3300.935 | 28779.0556 | 287.7906 | 29066.8462
| Installing solar collection devices on rooftops and considering vertical attachment of solar collection devices along the external layer of the opaque façades and additional overhangs for installing the collector at different tilt angles | Vertical Façade along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  |  | 90 | 0 | 1670 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | Rooftop and overhang features | Option 1 | Rooftop: Use Factor of 0,15 | 30 | 0 | 427.68 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | 88 | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 10.5 | 5.25 | 5.25 | 2118.68 | 270.4779 | 26.6331 | 629483.0661 | 8595.8418 | 1410.6737 | 10006.5155 | 54881.2022 | 872.4136 | 55753.6159 | 2118.68 | 88 | 186443.84 | 9.64 | 20424.0752 | 206867.9152 | 2068.6792 | 18035.6875 | 180.3569 | 18216.0444
|  |  | Option 2 | Rooftop: Use Factor of 0,15 | 30 | 0 | 427.68 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 10.5 | 5.25 | 5.25 | 2118.68 | 270.4779 | 26.6331 | 629483.0661 | 8595.8418 | 1410.6737 | 10006.5155 | 54881.2022 | 872.4136 | 55753.6159 | 2118.68 | 88 | 186443.84 | 9.64 | 20424.0752 | 206867.9152 | 2068.6792 | 18035.6875 | 180.3569 | 18216.0444
|  |  | Option 3 | Rooftop: Use Factor of 0,15 | 30 | 0 | 427.68 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 10.5 | 5.25 | 5.25 | 2118.68 | 270.4779 | 26.6331 | 629483.0661 | 8595.8418 | 1410.6737 | 10006.5155 | 54881.2022 | 872.4136 | 55753.6159 | 2118.68 | 88 | 186443.84 | 9.64 | 20424.0752 | 206867.9152 | 2068.6792 | 18035.6875 | 180.3569 | 18216.0444
|  |  | Option 4 | Rooftop: Use Factor of 0,25 | 30 | 0 | 712.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 10.5 | 5.25 | 5.25 | 2403.8 | 265.9067 | 24.3926 | 697821.4532 | 9587.7991 | 1465.8711 | 11053.6702 | 60839.2542 | 963.7093 | 61802.9636 | 2403.8 | 88 | 211534.4 | 9.64 | 23172.632 | 234707.032 | 2347.0703 | 20462.8286 | 204.6283 | 20667.4569
|  |  | Option 5 | Rooftop: Use Factor of 0,25 | 30 | 0 | 712.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 10.5 | 5.25 | 5.25 | 2403.8 | 265.9067 | 24.3926 | 697821.4532 | 9587.7991 | 1465.8711 | 11053.6702 | 60839.2542 | 963.7093 | 61802.9636 | 2403.8 | 88 | 211534.4 | 9.64 | 23172.632 | 234707.032 | 2347.0703 | 20462.8286 | 204.6283 | 20667.4569
|  |  | Option 6 | Rooftop: Use Factor of 0,25 | 30 | 0 | 712.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 10.5 | 5.25 | 5.25 | 2403.8 | 265.9067 | 24.3926 | 697821.4532 | 9587.7991 | 1465.8711 | 11053.6702 | 60839.2542 | 963.7093 | 61802.9636 | 2403.8 | 88 | 211534.4 | 9.64 | 23172.632 | 234707.032 | 2347.0703 | 20462.8286 | 204.6283 | 20667.4569
|  |  | Option 7 | Rooftop: Use Factor of 0,40 | 30 | 0 | 1140.48 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 10.5 | 5.25 | 5.25 | 2831.48 | 260.0931 | 21.7651 | 798075.8738 | 11046.7251 | 1540.6884 | 12587.4135 | 69579.8915 | 1097.4281 | 70677.3196 | 2831.48 | 88 | 249170.24 | 9.64 | 27295.4672 | 276465.7072 | 2764.6571 | 24103.5402 | 241.0354 | 24344.5756
|  |  | Option 8 | Rooftop: Use Factor of 0,40 | 30 | 0 | 1140.48 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 10.5 | 5.25 | 5.25 | 2831.48 | 260.0931 | 21.7651 | 798075.8738 | 11046.7251 | 1540.6884 | 12587.4135 | 69579.8915 | 1097.4281 | 70677.3196 | 2831.48 | 88 | 249170.24 | 9.64 | 27295.4672 | 276465.7072 | 2764.6571 | 24103.5402 | 241.0354 | 24344.5756
|  |  | Option 9 | Rooftop: Use Factor of 0,40 | 30 | 0 | 1140.48 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 10.5 | 5.25 | 5.25 | 2831.48 | 260.0931 | 21.7651 | 798075.8738 | 11046.7251 | 1540.6884 | 12587.4135 | 69579.8915 | 1097.4281 | 70677.3196 | 2831.48 | 88 | 249170.24 | 9.64 | 27295.4672 | 276465.7072 | 2764.6571 | 24103.5402 | 241.0354 | 24344.5756
|  |  | Option 10 | Rooftop: Use Factor of 0,5 | 30 | 0 | 1425.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 10.5 | 5.25 | 5.25 | 3116.6 | 256.746 | 20.3592 | 863626.0253 | 12002.6182 | 1586.2869 | 13588.9051 | 75294.8524 | 1184.7427 | 76479.5951 | 3116.6 | 88 | 274260.8 | 9.64 | 30044.024 | 304304.824 | 3043.0482 | 26530.6813 | 265.3068 | 26795.9881
|  |  | Option 11 | Rooftop: Use Factor of 0,5 | 30 | 0 | 1425.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 10.5 | 5.25 | 5.25 | 3116.6 | 256.746 | 20.3592 | 863626.0253 | 12002.6182 | 1586.2869 | 13588.9051 | 75294.8524 | 1184.7427 | 76479.5951 | 3116.6 | 88 | 274260.8 | 9.64 | 30044.024 | 304304.824 | 3043.0482 | 26530.6813 | 265.3068 | 26795.9881
|  |  | Option 12 | Rooftop: Use Factor of 0,5 | 30 | 0 | 1425.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 10.5 | 5.25 | 5.25 | 3116.6 | 256.746 | 20.3592 | 863626.0253 | 12002.6182 | 1586.2869 | 13588.9051 | 75294.8524 | 1184.7427 | 76479.5951 | 3116.6 | 88 | 274260.8 | 9.64 | 30044.024 | 304304.824 | 3043.0482 | 26530.6813 | 265.3068 | 26795.9881
|  |  | Option 13 | Rooftop: Use Factor of 0,6 | 30 | 0 | 1710.72 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 10.5 | 5.25 | 5.25 | 3401.72 | 253.7297 | 19.1558 | 928280.0906 | 12946.7609 | 1629.0674 | 14575.8283 | 80931.6884 | 1270.7871 | 82202.4756 | 3401.72 | 88 | 299351.36 | 9.64 | 32792.5808 | 332143.9408 | 3321.4394 | 28957.8223 | 289.5782 | 29247.4006
|  |  | Option 14 | Rooftop: Use Factor of 0,6 | 30 | 0 | 1710.72 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 10.5 | 5.25 | 5.25 | 3401.72 | 253.7297 | 19.1558 | 928280.0906 | 12946.7609 | 1629.0674 | 14575.8283 | 80931.6884 | 1270.7871 | 82202.4756 | 3401.72 | 88 | 299351.36 | 9.64 | 32792.5808 | 332143.9408 | 3321.4394 | 28957.8223 | 289.5782 | 29247.4006
|  |  | Option 15 | Rooftop: Use Factor of 0,6 | 30 | 0 | 1710.72 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 00) | 0 | 0 | 10.5 | 5.25 | 5.25 | 3401.72 | 253.7297 | 19.1558 | 928280.0906 | 12946.7609 | 1629.0674 | 14575.8283 | 80931.6884 | 1270.7871 | 82202.4756 | 3401.72 | 88 | 299351.36 | 9.64 | 32792.5808 | 332143.9408 | 3321.4394 | 28957.8223 | 289.5782 | 29247.4006
| Installing solar collection devices on rooftops and considering vertical attachment of solar collection devices along the external layer of the opaque façades and parapets of balconies and roofs and also additional overhangs for installing the collector at different tilt angles | Vertical Façade | Along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  | 90 | 0 | 1670 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  | Along parapets of balconies and roofs |  | 90 | 110.88 | 63.36 | 269.28 | 269.28 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | Rooftop and overhang features | Option 1 | Rooftop: Use Factor of 0,15 | 30 | 0 | 427.68 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 10.5 | 5.25 | 5.25 | 2831.48 | 260.0931 | 21.7651 | 798075.8738 | 11046.7251 | 1540.6884 | 12587.4135 | 69579.8915 | 1097.4281 | 70677.3196 | 2831.48 | 88 | 249170.24 | 9.64 | 27295.4672 | 276465.7072 | 2764.6571 | 24103.5402 | 241.0354 | 24344.5756
|  |  | Option 2 | Rooftop: Use Factor of 0,15 | 30 | 0 | 427.68 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 10.5 | 5.25 | 5.25 | 2831.48 | 260.0931 | 21.7651 | 798075.8738 | 11046.7251 | 1540.6884 | 12587.4135 | 69579.8915 | 1097.4281 | 70677.3196 | 2831.48 | 88 | 249170.24 | 9.64 | 27295.4672 | 276465.7072 | 2764.6571 | 24103.5402 | 241.0354 | 24344.5756
|  |  | Option 3 | Rooftop: Use Factor of 0,15 | 30 | 0 | 427.68 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 10.5 | 5.25 | 5.25 | 2831.48 | 260.0931 | 21.7651 | 798075.8738 | 11046.7251 | 1540.6884 | 12587.4135 | 69579.8915 | 1097.4281 | 70677.3196 | 2831.48 | 88 | 249170.24 | 9.64 | 27295.4672 | 276465.7072 | 2764.6571 | 24103.5402 | 241.0354 | 24344.5756
|  |  | Option 4 | Rooftop: Use Factor of 0,25 | 30 | 0 | 712.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 10.5 | 5.25 | 5.25 | 3116.6 | 256.746 | 20.3592 | 863626.0253 | 12002.6182 | 1586.2869 | 13588.9051 | 75294.8524 | 1184.7427 | 76479.5951 | 3116.6 | 88 | 274260.8 | 9.64 | 30044.024 | 304304.824 | 3043.0482 | 26530.6813 | 265.3068 | 26795.9881
|  |  | Option 5 | Rooftop: Use Factor of 0,25 | 30 | 0 | 712.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 10.5 | 5.25 | 5.25 | 3116.6 | 256.746 | 20.3592 | 863626.0253 | 12002.6182 | 1586.2869 | 13588.9051 | 75294.8524 | 1184.7427 | 76479.5951 | 3116.6 | 88 | 274260.8 | 9.64 | 30044.024 | 304304.824 | 3043.0482 | 26530.6813 | 265.3068 | 26795.9881
|  |  | Option 6 | Rooftop: Use Factor of 0,25 | 30 | 0 | 712.8 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 10.5 | 5.25 | 5.25 | 3116.6 | 256.746 | 20.3592 | 863626.0253 | 12002.6182 | 1586.2869 | 13588.9051 | 75294.8524 | 1184.7427 | 76479.5951 | 3116.6 | 88 | 274260.8 | 9.64 | 30044.024 | 304304.824 | 3043.0482 | 26530.6813 | 265.3068 | 26795.9881
|  |  | Option 7 | Rooftop: Use Factor of 0,40 | 30 | 0 | 1140.48 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 10.5 | 5.25 | 5.25 | 3544.28 | 252.3274 | 18.6162 | 960299.8305 | 13414.7817 | 1649.5262 | 15064.3079 | 83723.3153 | 1313.375 | 85036.6903 | 3544.28 | 88 | 311896.64 | 9.64 | 34166.8592 | 346063.4992 | 3460.635 | 30171.3929 | 301.7139 | 30473.1068
|  |  | Option 8 | Rooftop: Use Factor of 0,40 | 30 | 0 | 1140.48 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 10.5 | 5.25 | 5.25 | 3544.28 | 252.3274 | 18.6162 | 960299.8305 | 13414.7817 | 1649.5262 | 15064.3079 | 83723.3153 | 1313.375 | 85036.6903 | 3544.28 | 88 | 311896.64 | 9.64 | 34166.8592 | 346063.4992 | 3460.635 | 30171.3929 | 301.7139 | 30473.1068
|  |  | Option 9 | Rooftop: Use Factor of 0,40 | 30 | 0 | 1140.48 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 10.5 | 5.25 | 5.25 | 3544.28 | 252.3274 | 18.6162 | 960299.8305 | 13414.7817 | 1649.5262 | 15064.3079 | 83723.3153 | 1313.375 | 85036.6903 | 3544.28 | 88 | 311896.64 | 9.64 | 34166.8592 | 346063.4992 | 3460.635 | 30171.3929 | 301.7139 | 30473.1068
|  |  | Option 10 | Rooftop: Use Factor of 0,5 | 30 | 0 | 1425.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 10.5 | 5.25 | 5.25 | 3829.4 | 249.7054 | 17.6402 | 1023773.3324 | 14343.3288 | 1688.7853 | 16032.1141 | 89257.2244 | 1397.7528 | 90654.9772 | 3829.4 | 88 | 336987.2 | 9.64 | 36915.416 | 373902.616 | 3739.0262 | 32598.5339 | 325.9853 | 32924.5193
|  |  | Option 11 | Rooftop: Use Factor of 0,5 | 30 | 0 | 1425.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 10.5 | 5.25 | 5.25 | 3829.4 | 249.7054 | 17.6402 | 1023773.3324 | 14343.3288 | 1688.7853 | 16032.1141 | 89257.2244 | 1397.7528 | 90654.9772 | 3829.4 | 88 | 336987.2 | 9.64 | 36915.416 | 373902.616 | 3739.0262 | 32598.5339 | 325.9853 | 32924.5193
|  |  | Option 12 | Rooftop: Use Factor of 0,5 | 30 | 0 | 1425.6 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 10.5 | 5.25 | 5.25 | 3829.4 | 249.7054 | 17.6402 | 1023773.3324 | 14343.3288 | 1688.7853 | 16032.1141 | 89257.2244 | 1397.7528 | 90654.9772 | 3829.4 | 88 | 336987.2 | 9.64 | 36915.416 | 373902.616 | 3739.0262 | 32598.5339 | 325.9853 | 32924.5193
|  |  | Option 13 | Rooftop: Use Factor of 0,6 | 30 | 0 | 1710.72 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 10.5 | 5.25 | 5.25 | 4114.52 | 247.2962 | 16.7802 | 1086547.7209 | 15262.5802 | 1726.0594 | 16988.6396 | 94730.1817 | 1481.147 | 96211.3287 | 4114.52 | 88 | 362077.76 | 9.64 | 39663.9728 | 401741.7328 | 4017.4173 | 35025.675 | 350.2567 | 35375.9317
|  |  | Option 14 | Rooftop: Use Factor of 0,6 | 30 | 0 | 1710.72 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 10.5 | 5.25 | 5.25 | 4114.52 | 247.2962 | 16.7802 | 1086547.7209 | 15262.5802 | 1726.0594 | 16988.6396 | 94730.1817 | 1481.147 | 96211.3287 | 4114.52 | 88 | 362077.76 | 9.64 | 39663.9728 | 401741.7328 | 4017.4173 | 35025.675 | 350.2567 | 35375.9317
|  |  | Option 15 | Rooftop: Use Factor of 0,6 | 30 | 0 | 1710.72 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 00) | 0 | 0 | 10.5 | 5.25 | 5.25 | 4114.52 | 247.2962 | 16.7802 | 1086547.7209 | 15262.5802 | 1726.0594 | 16988.6396 | 94730.1817 | 1481.147 | 96211.3287 | 4114.52 | 88 | 362077.76 | 9.64 | 39663.9728 | 401741.7328 | 4017.4173 | 35025.675 | 350.2567 | 35375.9317

## Costs- Chillers
Note: Cells highlighted in yellow are the ones having solar fraction 1 or more (including losses)
Envelop Possibilities | Scenarios per configuration | Design features |  |  | Orientation of the Building Main Entrance to the North
[5 empty] | Thermally-Driven | [6 empty] | Electrically-driven
[5 empty] | Double-effect chillers with evacuated tubes collectors | [6 empty] | Water-cooled vapor compression chiller and Polycrystalline PV panel
[5 empty] | Building Level Total Design Cooling Requiremnts (kW) | Specific cost of DE absorption chillers [€/kW] | Investment cost of DE absorption chillers [€] | O&M cost of DE absorption chillers [€] | Total annualized investment cost of of DE absorption chillers [€/year] | Total annualized O&M cost of of DE absorption chillers [€/year] | Total annualized investment and O&M cost of of DE absorption chillers [€/year] | Building Level Total Design Cooling Requiremnts (kW) | Specific cost of Water-cooled VCC [€/kW] | Investment cost of Water-cooled VCC [€] | O&M cost of Water-cooled VCC [€] | Total annualized investment cost of of Water-cooled VCC [€/year] | Total annualized O&M cost of of Water-cooled VCC [€/year] | Total annualized investment and O&M cost of of Water-cooled VCC [€/year]
Roofs Tops | Installing solar collection devices on rooftops | On the top of flat roofs with a particular tilt angel and orientation | Option one: Use Factor of 0,15 |  | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option two: Use Factor of 0,25 |  | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option three: Use Factor of 0,40 |  | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option four: Use Factor of 0,50 |  | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option five: Use Factor of 0,6 |  | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
Flat Roofs & Façade | Installing solar collection devices on rooftops and considering vertical attachment of solar collection devices along the external layer of the opaque façades | Vertical Façade along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | On the top of flat roofs with a particular tilt angel and orientation | Option one: Use Factor of 0,15 |  | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option two: Use Factor of 0,25 |  | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option three: Use Factor of 0,40 |  | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option four: Use Factor of 0,50 |  | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option five: Use Factor of 0,6 |  | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
| Installing solar collection devices on rooftops and considering vertical attachment of solar collection devices along the external layer of the opaque façades and additional overhangs for installing the collector at different tilt angles | Vertical Façade along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | Rooftop and overhang features | Option 1 | Rooftop: Use Factor of 0,15 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 2 | Rooftop: Use Factor of 0,15 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 3 | Rooftop: Use Factor of 0,15 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 4 | Rooftop: Use Factor of 0,25 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 5 | Rooftop: Use Factor of 0,25 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 6 | Rooftop: Use Factor of 0,25 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 7 | Rooftop: Use Factor of 0,40 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 8 | Rooftop: Use Factor of 0,40 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 9 | Rooftop: Use Factor of 0,40 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 10 | Rooftop: Use Factor of 0,5 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 11 | Rooftop: Use Factor of 0,5 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 12 | Rooftop: Use Factor of 0,5 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 13 | Rooftop: Use Factor of 0,6 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 14 | Rooftop: Use Factor of 0,6 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 15 | Rooftop: Use Factor of 0,6 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 00) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
| Installing solar collection devices on rooftops and considering vertical attachment of solar collection devices along the external layer of the opaque façades and parapets of balconies and roofs and also additional overhangs for installing the collector at different tilt angles | Vertical Façade | Along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  | Along parapets of balconies and roofs |  | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  | Rooftop and overhang features | Option 1 | Rooftop: Use Factor of 0,15 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 2 | Rooftop: Use Factor of 0,15 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 3 | Rooftop: Use Factor of 0,15 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 4 | Rooftop: Use Factor of 0,25 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 5 | Rooftop: Use Factor of 0,25 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 6 | Rooftop: Use Factor of 0,25 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 7 | Rooftop: Use Factor of 0,40 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 8 | Rooftop: Use Factor of 0,40 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 9 | Rooftop: Use Factor of 0,40 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 10 | Rooftop: Use Factor of 0,5 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 11 | Rooftop: Use Factor of 0,5 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 12 | Rooftop: Use Factor of 0,5 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 13 | Rooftop: Use Factor of 0,6 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 14 | Rooftop: Use Factor of 0,6 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266
|  |  | Option 15 | Rooftop: Use Factor of 0,6 | - | - | - | - | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 00) | 1448.95 | 151.1416 | 218996.5591 | 6569.8968 | 19093.118 | 572.7935 | 19665.9115 | 1448.95 | 134.2068 | 194458.8909 | 5833.7667 | 16953.8122 | 508.6144 | 17462.4266

## Total LCC(AW) & LCOC for All
Note: Cells highlighted in yellow are the ones having solar fraction 1 or more (including losses)
Envelop Possibilities | Scenarios per configuration | Design features |  |  | Orientation of the Building Main Entrance to the North
[5 empty] | Thermally-Driven |  |  |  |  | Electrically-driven
[5 empty] | Double-effect chillers with evacuated tubes collectors |  |  |  |  | Water-cooled vapor compression chiller and Polycrystalline PV panel
[5 empty] | Total annualized investment and O&M cost of collectors [€/year] | Total annualized investment and O&M cost of of DE absorption chillers [€/year] | Total LCC (AW): Annualized investment and O&M cost of of Collectors & DE absorption chillers [€/year] | ESCOOLout (kWh/summer season) (including losses) | LCOC [€/kWh/year(summer)] | Total annualized investment and O&M cost of PV Panel system [€/year] | Total annualized investment and O&M cost of of Water-cooled VCC [€/year] | Total LCC (AW): Annualized investment and O&M cost of of PV panels system & Water-cooled VCC [€/year] | ESCOOLout (kWh/ year (summer)) | LCOC [€/kWh/year(summer)]
Roofs Tops | Installing solar collection devices on rooftops | On the top of flat roofs with a particular tilt angel and orientation | Option one: Use Factor of 0,15 |  | 15805.1589 | 19665.9115 | 35471.0704 | 185692.9694 | 0.19102 | 3677.1187 | 17462.4266 | 21139.5453 | 136174.8442 | 0.15524
|  |  | Option two: Use Factor of 0,25 |  | 23384.9265 | 19665.9115 | 43050.838 | 309488.2823 | 0.1391 | 6128.5312 | 17462.4266 | 23590.9578 | 226958.0737 | 0.10394
|  |  | Option three: Use Factor of 0,40 |  | 33855.3225 | 19665.9115 | 53521.234 | 495181.2517 | 0.10808 | 9805.6499 | 17462.4266 | 27268.0765 | 363132.9179 | 0.075091
|  |  | Option four: Use Factor of 0,50 |  | 40467.1756 | 19665.9115 | 60133.0871 | 618976.5647 | 0.097149 | 12257.0624 | 17462.4266 | 29719.489 | 453916.1474 | 0.065474
|  |  | Option five: Use Factor of 0,6 |  | 46871.0808 | 19665.9115 | 66536.9923 | 742771.8776 | 0.089579 | 14708.4749 | 17462.4266 | 32170.9015 | 544699.3769 | 0.059062
Flat Roofs & Façade | Installing solar collection devices on rooftops and considering vertical attachment of solar collection devices along the external layer of the opaque façades | Vertical Façade along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  |  | - | - | - | - | - | - | - | - | - | -
|  | On the top of flat roofs with a particular tilt angel and orientation | Option one: Use Factor of 0,15 |  | 55303.2937 | 19665.9115 | 74969.2053 | 511610.7345 | 0.14654 | 18035.49 | 17462.4266 | 35497.9167 | 375181.2053 | 0.094615
|  |  | Option two: Use Factor of 0,25 |  | 61361.3169 | 19665.9115 | 81027.2285 | 635406.0474 | 0.12752 | 20486.9025 | 17462.4266 | 37949.3291 | 465964.4348 | 0.081443
|  |  | Option three: Use Factor of 0,40 |  | 70246.5704 | 19665.9115 | 89912.482 | 821099.0168 | 0.1095 | 24164.0212 | 17462.4266 | 41626.4479 | 602139.279 | 0.069131
|  |  | Option four: Use Factor of 0,50 |  | 76055.0549 | 19665.9115 | 95720.9664 | 944894.3297 | 0.1013 | 26615.4337 | 17462.4266 | 44077.8603 | 692922.5085 | 0.063612
|  |  | Option five: Use Factor of 0,6 |  | 81783.4921 | 19665.9115 | 101449.4037 | 1068689.6426 | 0.094929 | 29066.8462 | 17462.4266 | 46529.2728 | 783705.7379 | 0.059371
| Installing solar collection devices on rooftops and considering vertical attachment of solar collection devices along the external layer of the opaque façades and additional overhangs for installing the collector at different tilt angles | Vertical Façade along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  |  | - | - | - | - | - | - | - | - | - | -
|  | Rooftop and overhang features | Option 1 | Rooftop: Use Factor of 0,15 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 55753.6159 | 19665.9115 | 75419.5274 | 518565.775 | 0.14544 | 18216.0444 | 17462.4266 | 35678.471 | 380281.5683 | 0.093821
|  |  | Option 2 | Rooftop: Use Factor of 0,15 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 55753.6159 | 19665.9115 | 75419.5274 | 520321.6559 | 0.14495 | 18216.0444 | 17462.4266 | 35678.471 | 381569.2143 | 0.093505
|  |  | Option 3 | Rooftop: Use Factor of 0,15 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 55753.6159 | 19665.9115 | 75419.5274 | 520646.4447 | 0.14486 | 18216.0444 | 17462.4266 | 35678.471 | 381807.3928 | 0.093446
|  |  | Option 4 | Rooftop: Use Factor of 0,25 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 61802.9636 | 19665.9115 | 81468.8751 | 642361.0879 | 0.12683 | 20667.4569 | 17462.4266 | 38129.8835 | 471064.7978 | 0.080944
|  |  | Option 5 | Rooftop: Use Factor of 0,25 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 61802.9636 | 19665.9115 | 81468.8751 | 644116.9688 | 0.12648 | 20667.4569 | 17462.4266 | 38129.8835 | 472352.4438 | 0.080723
|  |  | Option 6 | Rooftop: Use Factor of 0,25 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 61802.9636 | 19665.9115 | 81468.8751 | 644441.7576 | 0.12642 | 20667.4569 | 17462.4266 | 38129.8835 | 472590.6222 | 0.080683
|  |  | Option 7 | Rooftop: Use Factor of 0,40 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 70677.3196 | 19665.9115 | 90343.2311 | 828054.0573 | 0.1091 | 24344.5756 | 17462.4266 | 41807.0022 | 607239.642 | 0.068848
|  |  | Option 8 | Rooftop: Use Factor of 0,40 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 70677.3196 | 19665.9115 | 90343.2311 | 829809.9382 | 0.10887 | 24344.5756 | 17462.4266 | 41807.0022 | 608527.288 | 0.068702
|  |  | Option 9 | Rooftop: Use Factor of 0,40 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 70677.3196 | 19665.9115 | 90343.2311 | 830134.727 | 0.10883 | 24344.5756 | 17462.4266 | 41807.0022 | 608765.4665 | 0.068675
|  |  | Option 10 | Rooftop: Use Factor of 0,5 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 76479.5951 | 19665.9115 | 96145.5066 | 951849.3703 | 0.10101 | 26795.9881 | 17462.4266 | 44258.4147 | 698022.8715 | 0.063405
|  |  | Option 11 | Rooftop: Use Factor of 0,5 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 76479.5951 | 19665.9115 | 96145.5066 | 953605.2511 | 0.10082 | 26795.9881 | 17462.4266 | 44258.4147 | 699310.5175 | 0.063289
|  |  | Option 12 | Rooftop: Use Factor of 0,5 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 76479.5951 | 19665.9115 | 96145.5066 | 953930.0399 | 0.10079 | 26795.9881 | 17462.4266 | 44258.4147 | 699548.6959 | 0.063267
|  |  | Option 13 | Rooftop: Use Factor of 0,6 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 82202.4756 | 19665.9115 | 101868.3871 | 1075644.6832 | 0.094704 | 29247.4006 | 17462.4266 | 46709.8272 | 788806.101 | 0.059216
|  |  | Option 14 | Rooftop: Use Factor of 0,6 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 82202.4756 | 19665.9115 | 101868.3871 | 1077400.5641 | 0.09455 | 29247.4006 | 17462.4266 | 46709.8272 | 790093.747 | 0.059119
|  |  | Option 15 | Rooftop: Use Factor of 0,6 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 00) | 82202.4756 | 19665.9115 | 101868.3871 | 1077725.3529 | 0.094522 | 29247.4006 | 17462.4266 | 46709.8272 | 790331.9254 | 0.059102
| Installing solar collection devices on rooftops and considering vertical attachment of solar collection devices along the external layer of the opaque façades and parapets of balconies and roofs and also additional overhangs for installing the collector at different tilt angles | Vertical Façade | Along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  | - | - | - | - | - | - | - | - | - | -
|  |  | Along parapets of balconies and roofs |  | - | - | - | - | - | - | - | - | - | -
|  | Rooftop and overhang features | Option 1 | Rooftop: Use Factor of 0,15 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 70677.3196 | 19665.9115 | 90343.2311 | 663976.7098 | 0.13606 | 24344.5756 | 17462.4266 | 41807.0022 | 486916.2539 | 0.085861
|  |  | Option 2 | Rooftop: Use Factor of 0,15 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 70677.3196 | 19665.9115 | 90343.2311 | 665732.5907 | 0.1357 | 24344.5756 | 17462.4266 | 41807.0022 | 488203.8998 | 0.085634
|  |  | Option 3 | Rooftop: Use Factor of 0,15 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 70677.3196 | 19665.9115 | 90343.2311 | 666057.3795 | 0.13564 | 24344.5756 | 17462.4266 | 41807.0022 | 488442.0783 | 0.085593
|  |  | Option 4 | Rooftop: Use Factor of 0,25 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 76479.5951 | 19665.9115 | 96145.5066 | 787772.0228 | 0.12205 | 26795.9881 | 17462.4266 | 44258.4147 | 577699.4834 | 0.076611
|  |  | Option 5 | Rooftop: Use Factor of 0,25 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 76479.5951 | 19665.9115 | 96145.5066 | 789527.9036 | 0.12178 | 26795.9881 | 17462.4266 | 44258.4147 | 578987.1293 | 0.076441
|  |  | Option 6 | Rooftop: Use Factor of 0,25 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 76479.5951 | 19665.9115 | 96145.5066 | 789852.6924 | 0.12173 | 26795.9881 | 17462.4266 | 44258.4147 | 579225.3078 | 0.07641
|  |  | Option 7 | Rooftop: Use Factor of 0,40 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 85036.6903 | 19665.9115 | 104702.6018 | 973464.9921 | 0.10756 | 30473.1068 | 17462.4266 | 47935.5334 | 713874.3276 | 0.067148
|  |  | Option 8 | Rooftop: Use Factor of 0,40 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 85036.6903 | 19665.9115 | 104702.6018 | 975220.873 | 0.10736 | 30473.1068 | 17462.4266 | 47935.5334 | 715161.9736 | 0.067028
|  |  | Option 9 | Rooftop: Use Factor of 0,40 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 85036.6903 | 19665.9115 | 104702.6018 | 975545.6618 | 0.10733 | 30473.1068 | 17462.4266 | 47935.5334 | 715400.152 | 0.067005
|  |  | Option 10 | Rooftop: Use Factor of 0,5 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 90654.9772 | 19665.9115 | 110320.8887 | 1097260.3051 | 0.10054 | 32924.5193 | 17462.4266 | 50386.9459 | 804657.5571 | 0.062619
|  |  | Option 11 | Rooftop: Use Factor of 0,5 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 90654.9772 | 19665.9115 | 110320.8887 | 1099016.186 | 0.10038 | 32924.5193 | 17462.4266 | 50386.9459 | 805945.203 | 0.062519
|  |  | Option 12 | Rooftop: Use Factor of 0,5 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 90654.9772 | 19665.9115 | 110320.8887 | 1099340.9747 | 0.10035 | 32924.5193 | 17462.4266 | 50386.9459 | 806183.3815 | 0.062501
|  |  | Option 13 | Rooftop: Use Factor of 0,6 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 96211.3287 | 19665.9115 | 115877.2402 | 1221055.618 | 0.094899 | 35375.9317 | 17462.4266 | 52838.3584 | 895440.7865 | 0.059008
|  |  | Option 14 | Rooftop: Use Factor of 0,6 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 96211.3287 | 19665.9115 | 115877.2402 | 1222811.4989 | 0.094763 | 35375.9317 | 17462.4266 | 52838.3584 | 896728.4325 | 0.058923
|  |  | Option 15 | Rooftop: Use Factor of 0,6 | - | - | - | - | - | - | - | - | - | -
|  |  |  | Overhang (tilt angel of 00) | 96211.3287 | 19665.9115 | 115877.2402 | 1223136.2877 | 0.094738 | 35375.9317 | 17462.4266 | 52838.3584 | 896966.611 | 0.058908

## Key results
Scenarios Per Configuration and Key Design Features |  |  | SF(including losses) Value | LCC(AW)[€/year] | LCOC [€/kWh/year(summer)]
•DE absorption chillers with ETCs: Rooftops & Façade | C.I | Rooftop use factor of 0.50 | 1.0718 | 95720.9664 | 0.1013
|  | Rooftop use factor of 0.6 | 1.2156 | 101449.4037 | 0.094929
| C.II | Rooftop use factor of 0.50 &Overhang (tilt angel of 60) | 1.0798 | 96145.5066 | 0.10101
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 30) | 1.082 | 96145.5066 | 0.10082
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 0) | 1.0825 | 96145.5066 | 0.10079
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 60) | 1.2236 | 101868.3871 | 0.094704
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 30) | 1.2257 | 101868.3871 | 0.09455
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 0) | 1.2262 | 101868.3871 | 0.094522
| C.III | Rooftop use factor of 0.40 &Overhang (tilt angel of 60) | 1.1036 | 104702.6018 | 0.10756
|  | Rooftop use factor of 0.40 &Overhang (tilt angel of 30) | 1.1057 | 104702.6018 | 0.10736
|  | Rooftop use factor of 0.40 &Overhang (tilt angel of 0) | 1.1062 | 104702.6018 | 0.10733
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 60) | 1.2473 | 110320.8887 | 0.10054
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 30) | 1.2495 | 110320.8887 | 0.10038
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 0) | 1.2499 | 110320.8887 | 0.10035
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 60) | 1.391 | 115877.2402 | 0.094899
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 30) | 1.3932 | 115877.2402 | 0.094763
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 0) | 1.3937 | 115877.2402 | 0.094738
•Water-cooled VCC and PV panels: Rooftops & Façade | C.III | Rooftop use factor of 0.60 &Overhang (tilt angel of 60) | 1.0201 | 52838.3584 | 0.059008
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 30) | 1.0217 | 52838.3584 | 0.058923
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 0) | 1.022 | 52838.3584 | 0.058908

## Summary Charts of Key Results
Scenarios Per Configuration | LCC(AW)[€/year] | LCOC [€/kWh/year(summer)]
DE chillers&ETCs (C.I: 0.50 Roof-UF) | 95720.9664 | 0.1013
DE chillers&ETCs (C.I: 0.60 Roof-UF) | 101449.4037 | 0.094929
DE chillers&ETCs (C.II: 0.50 Roof-UF) | 96145.5066 | 0.10079
DE chillers&ETCs (C.II: 0.60 Roof-UF) | 101868.3871 | 0.094522
DE chillers&ETCs (C.III: 0.40 Roof-UF) | 104702.6018 | 0.10733
DE chillers&ETCs (C.III: 0.50 Roof-UF) | 110320.8887 | 0.10035
DE chillers&ETCs (C.III: 0.60 Roof-UF) | 115877.2402 | 0.094738
VCC&PV (C.III: 0.60 Roof-UF) | 52838.3584 | 0.058908