## COOLreq
Simulation Type | Item |  | Orientation of the Building Main Entrance
|  |  | North (N) | South (S) | East (E) | West (W)
Annual Whole Building (01 Jan to 31 Dec) | Annual Energy Per Conditioned Building Area | Building Annual Energy Use Intensity [kWh/m2/year] | 227.02 | 230.96 | 228.81 | 229.07
| Total Building Area [m2] |  | 13394.55 | 13394.55 | 13394.55 | 13394.55
| End Uses (Annual Building Utility) | Building Annual Cooling Demand [kWh/year] | 718042.33 | 770734.25 | 742135.53 | 745559.26
| Utility Use Per Conditioned Floor Area | Building Annual Cooling Demand Intensity [kWh/m2/year] | 53.61 | 57.54 | 55.41 | 55.66
Summer Design Week Whole Building (13-19 April) | Summer Deign Week Energy Per Conditioned Building Area | Building Summer Design Week Energy Use Intensity [kWh/m2/week] | 8.6 | 8.82 | 8.68 | 8.8
| Total Building Area [m2] |  | 13394.55 | 13394.55 | 13394.55 | 13394.55
| End Uses (Summer Design Week Building Utility) | Building Cooling Demand in Summer Design Week [kWh/week] | 68639.08 | 71608.31 | 69697.54 | 71315.71
|  | Building AVG Daily Cooling in Summer Design Week (kWh/day) (COOLreq) | 9805.5829 | 10229.7586 | 9956.7914 | 10187.9586
| Utility Use Per Conditioned Floor Area | Building Cooling Demand Intensity in Summer Design Week [kWh/m2/week] | 5.12 | 5.35 | 5.2 | 5.32

## SOLinput(July)
A tile angel of 90o | [5 empty] | Setup to calculate daily average solar irradiance at different orientations of the solar collection system considering the month of summer design week
Façade feature |  | Vertical Façade |  |  |  | Item | Description/Inputs
Orientation of the Opaque Façade |  | North (N) | South (S) | East (E) | West (W) | Assessment Tool | System Advisor Model | SAM 2023.12.17
Azimuth Angel |  | 0o | 180o | 90o | 270o | Location | Madrid, Spain | Weather Data Download - Madrid 082210 (IWEC)
Plane array irradiance (kWh/m2) in the Month of Madrid Summer Design Week (July) |  | 55.1956 | 95.8231 | 120.925 | 115.604 | Array Type | Fixed Roof Mount
SOLinput (kWh/m2/day) |  | 1.7805 | 3.0911 | 3.9008 | 3.7292 | Tilt Angels | 90°
A tile angel of 60o | [6 empty] | 60°
Façade feature |  | Vertical Façade/overhang |  |  |  |  | 30°
Orientation of the Opaque Façade |  | North (N) | South (S) | East (E) | West (W) |  | 0°
Azimuth Angel |  | 0o | 180o | 90o | 270o | Azimuth Angel | North (N) | 0o
Plane array irradiance (kWh/m2) in the Month of Madrid Summer Design Week (July) |  | 106.493 | 178.273 | 170.715 | 164.227 |  | South (S) | 180o
SOLinput (kWh/m2/day) |  | 3.4353 | 5.7507 | 5.5069 | 5.2976 |  | East (E) | 90o
A tile angel of 30o | [6 empty] | West (W) | 270o
Façade feature |  | Overhang |  |  |  | Month of Madrid Summer Design Week | July | Madrid Summer Design Week (13 to 19 July)
Orientation of the Overhang |  | North (N) | South (S) | East (E) | West (W)
Azimuth Angel |  | 0o | 180o | 90o | 270o
Plane array irradiance (kWh/m2) in the Month of Madrid Summer Design Week (July) |  | 187.807 | 228.445 | 213.554 | 208.367
SOLinput (kWh/m2/day) |  | 6.0583 | 7.3692 | 6.8888 | 6.7215
A tile angel of 0o
Façade feature |  | Overhang
Orientation of the Overhang |  | North (N) | South (S) | East (E) | West (W)
Azimuth Angel |  | 0o | 180o | 90o | 270o
Plane array irradiance (kWh/m2) in the Month of Madrid Summer Design Week (July) |  | 229.91 | 229.91 | 229.91 | 229.91
SOLinput (kWh/m2/day) |  | 7.4164 | 7.4164 | 7.4164 | 7.4164
SOLinput (kWh/m2/day) considering Orientation of the solar collection system
| Tilt Angel | North (N) | South (S) | East (E) | West (W)
| Surface tile angel of 90° | 1.7805 | 3.0911 | 3.9008 | 3.7292
| Surface tile angel of 60° | 3.4353 | 5.7507 | 5.5069 | 5.2976
| Surface tile angel of 30° | 6.0583 | 7.3692 | 6.8888 | 6.7215
| Surface tile angel of 0° | 7.4164 | 7.4164 | 7.4164 | 7.4164

## COPsolarsys &COPcoolsys
Item |  | Cooling technology device
|  | Thermally-Driven |  | Electrically-driven
|  | Flat-plate collectors (FPC) | Evacuated tubes collectors (ETC) | Polycrystalline panel
Efficiency (COPsolarsys) of the applied solar collection system, that can be either STC (Thermally-Driven) or PV panels (Electrically-driven) | Ranges | 0,40 to 0,80 | 0,55 to 0,75
| Assumed | 0.6 | 0.65 | 0.22
Item |  | Cooling technology device
|  | Thermally-Driven |  | Electrically-driven
|  | Single-effect chiller | Double-effect chiller | Water-cooled chiller
Coefficient of performance of the cooling technology | Ranges | COP: 0.5-0.75 Water-LiBr COP: 0.5-0.6 NH3-Water | COP: 0.8-1.2 Water-LiBr COP: 1.2-1.3 NH3-Water | -
| Assumed | 0.7 | 1.2 | 2.6

## SOLarray, SCOOLout, and SF
[12 empty] | COOLreq |  |  | 9805.58 |  | Note: Cells highlighted in yellow are the ones having solar fraction 1 or more
Envelop Possibilities | Scenarios per configuration | Design features |  |  | Orientation of the Building Main Entrance to the North
[5 empty] | Sureface Tilt angels | Area for collection Devcies Per Façade Orientation (STC/PV) | [7 empty] | Thermally-Driven | [14 empty] | Electrically-driven
[6 empty] | N |  | S |  | E |  | W |  | Single-effect chillers with flat-plate collectors |  |  |  |  | single-effect chillers with evacuated tubes collectors |  |  |  |  | Double-effect chillers with evacuated tubes collectors |  |  |  |  | Water-cooled vapor compression chiller and Polycrystalline PV panel
[6 empty] | SOLarry (N) (m2) | SOLinput (N) ((kWh/m2/day) | SOLarry (S) (m2) | SOLinput (S) ((kWh/m2/day) | SOLarry (E) (m2) | SOLinput (E) ((kWh/m2/day) | SOLarry (W) (m2) | SOLinput (W) ((kWh/m2/day) | COPcoolsys | COPsolarsys | SCOOLout (kWh/day) | SF (excluding losses) | SF (including losses) | COPcoolsys | COPsolarsys | SCOOLout (kWh/day) | SF (excluding losses) | SF (including losses) | COPcoolsys | COPsolarsys | SCOOLout (kWh/day) | SF (excluding losses) | SF (including losses) | COPcoolsys | COPsolarsys | SCOOLout (kWh/day) | SF (excluding losses) | SF (including losses)
Roofs Tops | Installing solar collection devices on rooftops | On the top of flat roofs with a particular tilt angel and orientation | Option one: Use Factor of 0,15 |  | 30 | 0 | 6.0583 | 427.68 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | 1323.6934 | 0.13499 | 0.11609 | 0.7 | 0.65 | 1434.0012 | 0.14624 | 0.12577 | 1.2 | 0.65 | 2458.2877 | 0.2507 | 0.2156 | 2.6 | 0.22 | 1802.7443 | 0.18385 | 0.15811
|  |  | Option two: Use Factor of 0,25 |  | 30 | 0 | 6.0583 | 712.8 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | 2206.1556 | 0.22499 | 0.19349 | 0.7 | 0.65 | 2390.0019 | 0.24374 | 0.20962 | 1.2 | 0.65 | 4097.1462 | 0.41784 | 0.35934 | 2.6 | 0.22 | 3004.5739 | 0.30641 | 0.26352
|  |  | Option three: Use Factor of 0,40 |  | 30 | 0 | 6.0583 | 1140.48 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | 3529.849 | 0.35998 | 0.30959 | 0.7 | 0.65 | 3824.0031 | 0.38998 | 0.33538 | 1.2 | 0.65 | 6555.4339 | 0.66854 | 0.57495 | 2.6 | 0.22 | 4807.3182 | 0.49026 | 0.42163
|  |  | Option four: Use Factor of 0,50 |  | 30 | 0 | 6.0583 | 1425.6 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | 4412.3113 | 0.44998 | 0.38698 | 0.7 | 0.65 | 4780.0039 | 0.48748 | 0.41923 | 1.2 | 0.65 | 8194.2923 | 0.83568 | 0.71868 | 2.6 | 0.22 | 6009.1477 | 0.61283 | 0.52703
|  |  | Option five: Use Factor of 0,6 |  | 30 | 0 | 6.0583 | 1710.72 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | 5294.7735 | 0.53998 | 0.46438 | 0.7 | 0.65 | 5736.0046 | 0.58497 | 0.50308 | 1.2 | 0.65 | 9833.1508 | 1.0028 | 0.86242 | 2.6 | 0.22 | 7210.9773 | 0.7354 | 0.63244
Façade ony (opaque façade/overhangs/parapets of balconies) | Only vertical attachment of solar collection devices along the external layer of the opaque façades (worst case scenario) | Vertical Façade along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  |  | 90 | 0 | 1.7805 | 1670 | 3.0911 | 0 | 3.9008 | 0 | 3.7292 | 0.7 | 0.6 | 2168.0765 | 0.22111 | 0.19015 | 0.7 | 0.65 | 2348.7495 | 0.23953 | 0.206 | 1.2 | 0.65 | 4026.4278 | 0.41063 | 0.35314 | 2.6 | 0.22 | 2952.7137 | 0.30113 | 0.25897
| Vertical attachment of solar collection devices along the external layer of the opaque façades and additional overhangs for installing the collector at different tilt angles | Vertical Façade along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  |  | 90 | 0 | 1.7805 | 1670 | 3.0911 | 0 | 3.9008 | 0 | 3.7292 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  | Overhang | Option one |  | 60 | 0 | 3.4353 | 10.5 | 5.7507 | 5.25 | 5.5069 | 5.25 | 5.2976 | 0.7 | 0.6 | 2217.2613 | 0.22612 | 0.19447 | 0.7 | 0.65 | 2402.0331 | 0.24497 | 0.21067 | 1.2 | 0.65 | 4117.7711 | 0.41994 | 0.36115 | 2.6 | 0.22 | 3019.6988 | 0.30796 | 0.26484
|  |  | Option two |  | 30 | 0 | 6.0583 | 10.5 | 7.3692 | 5.25 | 6.8888 | 5.25 | 6.7215 | 0.7 | 0.6 | 2230.5854 | 0.22748 | 0.19563 | 0.7 | 0.65 | 2416.4675 | 0.24644 | 0.21194 | 1.2 | 0.65 | 4142.5157 | 0.42247 | 0.36332 | 2.6 | 0.22 | 3037.8449 | 0.30981 | 0.26643
|  |  | Option three |  | 0 | 0 | 7.4164 | 10.5 | 7.4164 | 5.25 | 7.4164 | 5.25 | 7.4164 | 0.7 | 0.6 | 2233.4895 | 0.22778 | 0.19589 | 0.7 | 0.65 | 2419.6136 | 0.24676 | 0.21221 | 1.2 | 0.65 | 4147.9091 | 0.42302 | 0.36379 | 2.6 | 0.22 | 3041.8 | 0.31021 | 0.26678
| Vertical attachment ofsolar collection devices along the external layer of the opaque façades and parapets of balconies and roofs and also additional overhangs for installing the collector at different tilt angles | Vertical Façade | Along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  | 90 | 0 | 1.7805 | 1670 | 3.0911 | 0 | 3.9008 | 0 | 3.7292 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  | Along parapets of balconies and roofs |  | 90 | 110.88 | 1.7805 | 63.36 | 3.0911 | 269.28 | 3.9008 | 269.28 | 3.7292 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  | Overhang | Option one |  | 60 | 0 | 3.4353 | 10.5 | 5.7507 | 5.25 | 5.5069 | 5.25 | 5.2976 | 0.7 | 0.6 | 3245.3692 | 0.33097 | 0.28464 | 0.7 | 0.65 | 3515.8166 | 0.35855 | 0.30836 | 1.2 | 0.65 | 6027.1141 | 0.61466 | 0.52861 | 2.6 | 0.22 | 4419.8837 | 0.45075 | 0.38765
|  |  | Option two |  | 30 | 0 | 6.0583 | 10.5 | 7.3692 | 5.25 | 6.8888 | 5.25 | 6.7215 | 0.7 | 0.6 | 3258.6932 | 0.33233 | 0.2858 | 0.7 | 0.65 | 3530.251 | 0.36002 | 0.30962 | 1.2 | 0.65 | 6051.8588 | 0.61719 | 0.53078 | 2.6 | 0.22 | 4438.0298 | 0.4526 | 0.38924
|  |  | Option three |  | 0 | 0 | 7.4164 | 10.5 | 7.4164 | 5.25 | 7.4164 | 5.25 | 7.4164 | 0.7 | 0.6 | 3261.5973 | 0.33263 | 0.28606 | 0.7 | 0.65 | 3533.3971 | 0.36035 | 0.3099 | 1.2 | 0.65 | 6057.2521 | 0.61774 | 0.53125 | 2.6 | 0.22 | 4441.9849 | 0.45301 | 0.38959
Flat Roofs & Façade | Installing solar collection devices on rooftops and considering vertical attachment of solar collection devices along the external layer of the opaque façades | Vertical Façade along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  |  | 90 | 0 | 1.7805 | 1670 | 3.0911 | 0 | 3.9008 | 0 | 3.7292 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  | On the top of flat roofs with a particular tilt angel and orientation | Option one: Use Factor of 0,15 |  | 30 | 0 | 6.0583 | 427.68 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | 3491.7699 | 0.3561 | 0.30625 | 0.7 | 0.65 | 3782.7507 | 0.38578 | 0.33177 | 1.2 | 0.65 | 6484.7155 | 0.66133 | 0.56874 | 2.6 | 0.22 | 4755.458 | 0.48497 | 0.41708
|  |  | Option two: Use Factor of 0,25 |  | 30 | 0 | 6.0583 | 712.8 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | 4374.2321 | 0.4461 | 0.38364 | 0.7 | 0.65 | 4738.7515 | 0.48327 | 0.41561 | 1.2 | 0.65 | 8123.574 | 0.82846 | 0.71248 | 2.6 | 0.22 | 5957.2876 | 0.60754 | 0.52248
|  |  | Option three: Use Factor of 0,40 |  | 30 | 0 | 6.0583 | 1140.48 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | 5697.9255 | 0.58109 | 0.49974 | 0.7 | 0.65 | 6172.7526 | 0.62951 | 0.54138 | 1.2 | 0.65 | 10581.8617 | 1.0792 | 0.92808 | 2.6 | 0.22 | 7760.0319 | 0.79139 | 0.68059
|  |  | Option four: Use Factor of 0,50 |  | 30 | 0 | 6.0583 | 1425.6 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | 6580.3878 | 0.67109 | 0.57713 | 0.7 | 0.65 | 7128.7534 | 0.72701 | 0.62523 | 1.2 | 0.65 | 12220.7201 | 1.2463 | 1.0718 | 2.6 | 0.22 | 8961.8614 | 0.91396 | 0.786
|  |  | Option five: Use Factor of 0,6 |  | 30 | 0 | 6.0583 | 1710.72 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | 7462.85 | 0.76108 | 0.65453 | 0.7 | 0.65 | 8084.7542 | 0.82451 | 0.70907 | 1.2 | 0.65 | 13859.5786 | 1.4134 | 1.2156 | 2.6 | 0.22 | 10163.691 | 1.0365 | 0.89141
| Installing solar collection devices on rooftops and considering vertical attachment of solar collection devices along the external layer of the opaque façades and additional overhangs for installing the collector at different tilt angles | Vertical Façade along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  |  | 90 | 0 | 1.7805 | 1670 | 3.0911 | 0 | 3.9008 | 0 | 3.7292 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  | Rooftop and overhang features | Option 1 | Rooftop: Use Factor of 0,15 | 30 | 0 | 6.0583 | 427.68 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 3.4353 | 10.5 | 5.7507 | 5.25 | 5.5069 | 5.25 | 5.2976 | 0.7 | 0.6 | 3540.9547 | 0.36112 | 0.31056 | 0.7 | 0.65 | 3836.0343 | 0.39121 | 0.33644 | 1.2 | 0.65 | 6576.0588 | 0.67064 | 0.57675 | 2.6 | 0.22 | 4822.4431 | 0.49181 | 0.42295
|  |  | Option 2 | Rooftop: Use Factor of 0,15 | 30 | 0 | 6.0583 | 427.68 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 6.0583 | 10.5 | 7.3692 | 5.25 | 6.8888 | 5.25 | 6.7215 | 0.7 | 0.6 | 3554.2788 | 0.36248 | 0.31173 | 0.7 | 0.65 | 3850.4687 | 0.39268 | 0.33771 | 1.2 | 0.65 | 6600.8034 | 0.67317 | 0.57892 | 2.6 | 0.22 | 4840.5892 | 0.49366 | 0.42454
|  |  | Option 3 | Rooftop: Use Factor of 0,15 | 30 | 0 | 6.0583 | 427.68 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 7.4164 | 10.5 | 7.4164 | 5.25 | 7.4164 | 5.25 | 7.4164 | 0.7 | 0.6 | 3557.1829 | 0.36277 | 0.31198 | 0.7 | 0.65 | 3853.6148 | 0.393 | 0.33798 | 1.2 | 0.65 | 6606.1968 | 0.67372 | 0.5794 | 2.6 | 0.22 | 4844.5443 | 0.49406 | 0.42489
|  |  | Option 4 | Rooftop: Use Factor of 0,25 | 30 | 0 | 6.0583 | 712.8 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 3.4353 | 10.5 | 5.7507 | 5.25 | 5.5069 | 5.25 | 5.2976 | 0.7 | 0.6 | 4423.417 | 0.45111 | 0.38796 | 0.7 | 0.65 | 4792.0351 | 0.4887 | 0.42029 | 1.2 | 0.65 | 8214.9172 | 0.83778 | 0.72049 | 2.6 | 0.22 | 6024.2726 | 0.61437 | 0.52836
|  |  | Option 5 | Rooftop: Use Factor of 0,25 | 30 | 0 | 6.0583 | 712.8 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 6.0583 | 10.5 | 7.3692 | 5.25 | 6.8888 | 5.25 | 6.7215 | 0.7 | 0.6 | 4436.741 | 0.45247 | 0.38913 | 0.7 | 0.65 | 4806.4694 | 0.49018 | 0.42155 | 1.2 | 0.65 | 8239.6619 | 0.8403 | 0.72266 | 2.6 | 0.22 | 6042.4187 | 0.61622 | 0.52995
|  |  | Option 6 | Rooftop: Use Factor of 0,25 | 30 | 0 | 6.0583 | 712.8 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 7.4164 | 10.5 | 7.4164 | 5.25 | 7.4164 | 5.25 | 7.4164 | 0.7 | 0.6 | 4439.6451 | 0.45277 | 0.38938 | 0.7 | 0.65 | 4809.6156 | 0.4905 | 0.42183 | 1.2 | 0.65 | 8245.0552 | 0.84085 | 0.72313 | 2.6 | 0.22 | 6046.3738 | 0.61663 | 0.5303
|  |  | Option 7 | Rooftop: Use Factor of 0,40 | 30 | 0 | 6.0583 | 1140.48 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 3.4353 | 10.5 | 5.7507 | 5.25 | 5.5069 | 5.25 | 5.2976 | 0.7 | 0.6 | 5747.1103 | 0.58611 | 0.50405 | 0.7 | 0.65 | 6226.0362 | 0.63495 | 0.54606 | 1.2 | 0.65 | 10673.2049 | 1.0885 | 0.9361 | 2.6 | 0.22 | 7827.017 | 0.79822 | 0.68647
|  |  | Option 8 | Rooftop: Use Factor of 0,40 | 30 | 0 | 6.0583 | 1140.48 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 6.0583 | 10.5 | 7.3692 | 5.25 | 6.8888 | 5.25 | 6.7215 | 0.7 | 0.6 | 5760.4344 | 0.58746 | 0.50522 | 0.7 | 0.65 | 6240.4706 | 0.63642 | 0.54732 | 1.2 | 0.65 | 10697.9496 | 1.091 | 0.93827 | 2.6 | 0.22 | 7845.163 | 0.80007 | 0.68806
|  |  | Option 9 | Rooftop: Use Factor of 0,40 | 30 | 0 | 6.0583 | 1140.48 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 7.4164 | 10.5 | 7.4164 | 5.25 | 7.4164 | 5.25 | 7.4164 | 0.7 | 0.6 | 5763.3385 | 0.58776 | 0.50547 | 0.7 | 0.65 | 6243.6167 | 0.63674 | 0.5476 | 1.2 | 0.65 | 10703.3429 | 1.0916 | 0.93874 | 2.6 | 0.22 | 7849.1182 | 0.80047 | 0.68841
|  |  | Option 10 | Rooftop: Use Factor of 0,5 | 30 | 0 | 6.0583 | 1425.6 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 3.4353 | 10.5 | 5.7507 | 5.25 | 5.5069 | 5.25 | 5.2976 | 0.7 | 0.6 | 6629.5726 | 0.6761 | 0.58145 | 0.7 | 0.65 | 7182.037 | 0.73244 | 0.6299 | 1.2 | 0.65 | 12312.0634 | 1.2556 | 1.0798 | 2.6 | 0.22 | 9028.8465 | 0.92079 | 0.79188
|  |  | Option 11 | Rooftop: Use Factor of 0,5 | 30 | 0 | 6.0583 | 1425.6 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 6.0583 | 10.5 | 7.3692 | 5.25 | 6.8888 | 5.25 | 6.7215 | 0.7 | 0.6 | 6642.8966 | 0.67746 | 0.58262 | 0.7 | 0.65 | 7196.4714 | 0.73392 | 0.63117 | 1.2 | 0.65 | 12336.8081 | 1.2581 | 1.082 | 2.6 | 0.22 | 9046.9926 | 0.92264 | 0.79347
|  |  | Option 12 | Rooftop: Use Factor of 0,5 | 30 | 0 | 6.0583 | 1425.6 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 7.4164 | 10.5 | 7.4164 | 5.25 | 7.4164 | 5.25 | 7.4164 | 0.7 | 0.6 | 6645.8008 | 0.67776 | 0.58287 | 0.7 | 0.65 | 7199.6175 | 0.73424 | 0.63144 | 1.2 | 0.65 | 12342.2014 | 1.2587 | 1.0825 | 2.6 | 0.22 | 9050.9477 | 0.92304 | 0.79381
|  |  | Option 13 | Rooftop: Use Factor of 0,6 | 30 | 0 | 6.0583 | 1710.72 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 3.4353 | 10.5 | 5.7507 | 5.25 | 5.5069 | 5.25 | 5.2976 | 0.7 | 0.6 | 7512.0349 | 0.7661 | 0.65884 | 0.7 | 0.65 | 8138.0378 | 0.82994 | 0.71375 | 1.2 | 0.65 | 13950.9219 | 1.4228 | 1.2236 | 2.6 | 0.22 | 10230.676 | 1.0434 | 0.89728
|  |  | Option 14 | Rooftop: Use Factor of 0,6 | 30 | 0 | 6.0583 | 1710.72 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 6.0583 | 10.5 | 7.3692 | 5.25 | 6.8888 | 5.25 | 6.7215 | 0.7 | 0.6 | 7525.3589 | 0.76746 | 0.66001 | 0.7 | 0.65 | 8152.4721 | 0.83141 | 0.71501 | 1.2 | 0.65 | 13975.6665 | 1.4253 | 1.2257 | 2.6 | 0.22 | 10248.8221 | 1.0452 | 0.89887
|  |  | Option 15 | Rooftop: Use Factor of 0,6 | 30 | 0 | 6.0583 | 1710.72 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 00) | 0 | 0 | 7.4164 | 10.5 | 7.4164 | 5.25 | 7.4164 | 5.25 | 7.4164 | 0.7 | 0.6 | 7528.263 | 0.76775 | 0.66027 | 0.7 | 0.65 | 8155.6183 | 0.83173 | 0.71529 | 1.2 | 0.65 | 13981.0599 | 1.4258 | 1.2262 | 2.6 | 0.22 | 10252.7772 | 1.0456 | 0.89922
| Installing solar collection devices on rooftops and considering vertical attachment of solar collection devices along the external layer of the opaque façades and parapets of balconies and roofs and also additional overhangs for installing the collector at different tilt angles | Vertical Façade | Along the external layer of the opaque façades (Backside of the building-opposite to the main entrance) |  | 90 | 0 | 1.7805 | 1670 | 3.0911 | 0 | 3.9008 | 0 | 3.7292 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  | Along parapets of balconies and roofs |  | 90 | 110.88 | 1.7805 | 63.36 | 3.0911 | 269.28 | 3.9008 | 269.28 | 3.7292 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  | Rooftop and overhang features | Option 1 | Rooftop: Use Factor of 0,15 | 30 | 0 | 6.0583 | 427.68 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 3.4353 | 10.5 | 5.7507 | 5.25 | 5.5069 | 5.25 | 5.2976 | 0.7 | 0.6 | 4569.0625 | 0.46597 | 0.40073 | 0.7 | 0.65 | 4949.8177 | 0.5048 | 0.43412 | 1.2 | 0.65 | 8485.4018 | 0.86536 | 0.74421 | 2.6 | 0.22 | 6222.628 | 0.6346 | 0.54576
|  |  | Option 2 | Rooftop: Use Factor of 0,15 | 30 | 0 | 6.0583 | 427.68 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 6.0583 | 10.5 | 7.3692 | 5.25 | 6.8888 | 5.25 | 6.7215 | 0.7 | 0.6 | 4582.3866 | 0.46732 | 0.4019 | 0.7 | 0.65 | 4964.2521 | 0.50627 | 0.43539 | 1.2 | 0.65 | 8510.1465 | 0.86789 | 0.74638 | 2.6 | 0.22 | 6240.7741 | 0.63645 | 0.54735
|  |  | Option 3 | Rooftop: Use Factor of 0,15 | 30 | 0 | 6.0583 | 427.68 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 7.4164 | 10.5 | 7.4164 | 5.25 | 7.4164 | 5.25 | 7.4164 | 0.7 | 0.6 | 4585.2907 | 0.46762 | 0.40215 | 0.7 | 0.65 | 4967.3982 | 0.50659 | 0.43567 | 1.2 | 0.65 | 8515.5399 | 0.86844 | 0.74686 | 2.6 | 0.22 | 6244.7292 | 0.63685 | 0.54769
|  |  | Option 4 | Rooftop: Use Factor of 0,25 | 30 | 0 | 6.0583 | 712.8 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 3.4353 | 10.5 | 5.7507 | 5.25 | 5.5069 | 5.25 | 5.2976 | 0.7 | 0.6 | 5451.5248 | 0.55596 | 0.47813 | 0.7 | 0.65 | 5905.8185 | 0.60229 | 0.51797 | 1.2 | 0.65 | 10124.2603 | 1.0325 | 0.88795 | 2.6 | 0.22 | 7424.4576 | 0.75717 | 0.65116
|  |  | Option 5 | Rooftop: Use Factor of 0,25 | 30 | 0 | 6.0583 | 712.8 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 6.0583 | 10.5 | 7.3692 | 5.25 | 6.8888 | 5.25 | 6.7215 | 0.7 | 0.6 | 5464.8488 | 0.55732 | 0.4793 | 0.7 | 0.65 | 5920.2529 | 0.60376 | 0.51924 | 1.2 | 0.65 | 10149.005 | 1.035 | 0.89012 | 2.6 | 0.22 | 7442.6036 | 0.75902 | 0.65275
|  |  | Option 6 | Rooftop: Use Factor of 0,25 | 30 | 0 | 6.0583 | 712.8 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 7.4164 | 10.5 | 7.4164 | 5.25 | 7.4164 | 5.25 | 7.4164 | 0.7 | 0.6 | 5467.7529 | 0.55762 | 0.47955 | 0.7 | 0.65 | 5923.399 | 0.60408 | 0.51951 | 1.2 | 0.65 | 10154.3983 | 1.0356 | 0.89059 | 2.6 | 0.22 | 7446.5588 | 0.75942 | 0.6531
|  |  | Option 7 | Rooftop: Use Factor of 0,40 | 30 | 0 | 6.0583 | 1140.48 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 3.4353 | 10.5 | 5.7507 | 5.25 | 5.5069 | 5.25 | 5.2976 | 0.7 | 0.6 | 6775.2182 | 0.69096 | 0.59422 | 0.7 | 0.65 | 7339.8197 | 0.74853 | 0.64374 | 1.2 | 0.65 | 12582.548 | 1.2832 | 1.1036 | 2.6 | 0.22 | 9227.2019 | 0.94102 | 0.80927
|  |  | Option 8 | Rooftop: Use Factor of 0,40 | 30 | 0 | 6.0583 | 1140.48 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 6.0583 | 10.5 | 7.3692 | 5.25 | 6.8888 | 5.25 | 6.7215 | 0.7 | 0.6 | 6788.5422 | 0.69231 | 0.59539 | 0.7 | 0.65 | 7354.2541 | 0.75001 | 0.64501 | 1.2 | 0.65 | 12607.2927 | 1.2857 | 1.1057 | 2.6 | 0.22 | 9245.348 | 0.94287 | 0.81086
|  |  | Option 9 | Rooftop: Use Factor of 0,40 | 30 | 0 | 6.0583 | 1140.48 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 7.4164 | 10.5 | 7.4164 | 5.25 | 7.4164 | 5.25 | 7.4164 | 0.7 | 0.6 | 6791.4463 | 0.69261 | 0.59564 | 0.7 | 0.65 | 7357.4002 | 0.75033 | 0.64528 | 1.2 | 0.65 | 12612.686 | 1.2863 | 1.1062 | 2.6 | 0.22 | 9249.3031 | 0.94327 | 0.81121
|  |  | Option 10 | Rooftop: Use Factor of 0,5 | 30 | 0 | 6.0583 | 1425.6 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 3.4353 | 10.5 | 5.7507 | 5.25 | 5.5069 | 5.25 | 5.2976 | 0.7 | 0.6 | 7657.6804 | 0.78095 | 0.67162 | 0.7 | 0.65 | 8295.8204 | 0.84603 | 0.72759 | 1.2 | 0.65 | 14221.4065 | 1.4503 | 1.2473 | 2.6 | 0.22 | 10429.0314 | 1.0636 | 0.91468
|  |  | Option 11 | Rooftop: Use Factor of 0,5 | 30 | 0 | 6.0583 | 1425.6 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 6.0583 | 10.5 | 7.3692 | 5.25 | 6.8888 | 5.25 | 6.7215 | 0.7 | 0.6 | 7671.0045 | 0.78231 | 0.67279 | 0.7 | 0.65 | 8310.2548 | 0.8475 | 0.72885 | 1.2 | 0.65 | 14246.1511 | 1.4529 | 1.2495 | 2.6 | 0.22 | 10447.1775 | 1.0654 | 0.91627
|  |  | Option 12 | Rooftop: Use Factor of 0,5 | 30 | 0 | 6.0583 | 1425.6 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 0) | 0 | 0 | 7.4164 | 10.5 | 7.4164 | 5.25 | 7.4164 | 5.25 | 7.4164 | 0.7 | 0.6 | 7673.9086 | 0.78261 | 0.67304 | 0.7 | 0.65 | 8313.401 | 0.84782 | 0.72913 | 1.2 | 0.65 | 14251.5445 | 1.4534 | 1.2499 | 2.6 | 0.22 | 10451.1326 | 1.0658 | 0.91662
|  |  | Option 13 | Rooftop: Use Factor of 0,6 | 30 | 0 | 6.0583 | 1710.72 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 60) | 60 | 0 | 3.4353 | 10.5 | 5.7507 | 5.25 | 5.5069 | 5.25 | 5.2976 | 0.7 | 0.6 | 8540.1427 | 0.87095 | 0.74901 | 0.7 | 0.65 | 9251.8212 | 0.94353 | 0.81143 | 1.2 | 0.65 | 15860.265 | 1.6175 | 1.391 | 2.6 | 0.22 | 11630.861 | 1.1861 | 1.0201
|  |  | Option 14 | Rooftop: Use Factor of 0,6 | 30 | 0 | 6.0583 | 1710.72 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 30) | 30 | 0 | 6.0583 | 10.5 | 7.3692 | 5.25 | 6.8888 | 5.25 | 6.7215 | 0.7 | 0.6 | 8553.4667 | 0.87231 | 0.75018 | 0.7 | 0.65 | 9266.2556 | 0.945 | 0.8127 | 1.2 | 0.65 | 15885.0096 | 1.62 | 1.3932 | 2.6 | 0.22 | 11649.007 | 1.188 | 1.0217
|  |  | Option 15 | Rooftop: Use Factor of 0,6 | 30 | 0 | 6.0583 | 1710.72 | 7.3692 | 0 | 6.8888 | 0 | 6.7215 | 0.7 | 0.6 | - | - | - | 0.7 | 0.65 | - | - | - | 1.2 | 0.65 | - | - | - | 2.6 | 0.22 | - | - | -
|  |  |  | Overhang (tilt angel of 00) | 0 | 0 | 7.4164 | 10.5 | 7.4164 | 5.25 | 7.4164 | 5.25 | 7.4164 | 0.7 | 0.6 | 8556.3708 | 0.8726 | 0.75044 | 0.7 | 0.65 | 9269.4017 | 0.94532 | 0.81297 | 1.2 | 0.65 | 15890.403 | 1.6205 | 1.3937 | 2.6 | 0.22 | 11652.9622 | 1.1884 | 1.022

## General Summary
Envelope application Possibilities |  | SF (excluding losses) Values |  |  |  | Envelope application Possibilities |  | SF (including losses) Values
|  | Thermally Driven |  |  | Electrically Driven |  |  | Thermally Driven |  |  | Electrically Driven
| Use Factor (UF) of Flat Roof | SE Absorption Chillers& FPCs | SE Absorption Chillers& ETCs | DE Absorption Chillers& ETCs | Water-cooled VCC & PV panel |  | Use Factor (UF) of Flat Roof | SE Absorption Chillers& FPCs | SE Absorption Chillers& ETCs | DE Absorption Chillers& ETCs | Water-cooled VCC & PV panel
A. Rooftops | UF: 0.25 | 0.22499 | 0.24374 | 0.41784 | 0.30641 | A. Rooftops | UF: 0.25 | 0.19349 | 0.20962 | 0.35934 | 0.26352
| UF: 0.40 | 0.35998 | 0.38998 | 0.66854 | 0.49026 |  | UF: 0.40 | 0.30959 | 0.33538 | 0.57495 | 0.42163
| UF: 0.50 | 0.44998 | 0.48748 | 0.83568 | 0.61283 |  | UF: 0.50 | 0.38698 | 0.41923 | 0.71868 | 0.52703
| UF: 0.6 | 0.53998 | 0.58497 | 1.0028 | 0.7354 |  | UF: 0.6 | 0.46438 | 0.50308 | 0.86242 | 0.63244
Envelope application Possibilities |  | SF (excluding losses) Values |  |  |  | Envelope application Possibilities |  | SF (including losses) Values
|  | Thermally Driven |  |  | Electrically Driven |  |  | Thermally Driven |  |  | Electrically Driven
| Scenarios Per Configuration | SE Absorption Chillers& FPCs | SE Absorption Chillers& ETCs | DE Absorption Chillers& ETCs | Water-cooled VCC & PV panel |  | Scenarios Per Configuration | SE Absorption Chillers& FPCs | SE Absorption Chillers& ETCs | DE Absorption Chillers& ETCs | Water-cooled VCC & PV panel
B. Façade only | B.I. | 0.221 | 0.24 | 0.411 | 0.301 | B. Façade only | B.I. | 0.19015 | 0.206 | 0.35314 | 0.25897
| B.II. | 0.228 | 0.247 | 0.423 | 0.31 |  | B.II. | 0.19589 | 0.21221 | 0.36379 | 0.26678
| B.III. | 0.333 | 0.36 | 0.618 | 0.453 |  | B.III. | 0.28606 | 0.3099 | 0.53125 | 0.38959
Envelope application Possibilities |  | SF (excluding losses) Values |  |  |  | Envelope application Possibilities |  | SF (including losses) Values
|  | Thermally Driven |  |  | Electrically Driven |  |  | Thermally Driven |  |  | Electrically Driven
| Scenarios Per Configuration | SE Absorption Chillers& FPCs | SE Absorption Chillers& ETCs | DE Absorption Chillers& ETCs | Water-cooled VCC & PV panel |  | Scenarios Per Configuration | SE Absorption Chillers& FPCs | SE Absorption Chillers& ETCs | DE Absorption Chillers& ETCs | Water-cooled VCC & PV panel
C. Rooftops & Façade | C.I. | 0.761 | 0.825 | 1.413 | 1.037 | C. Rooftops & Façade | C.I. | 0.65453 | 0.70907 | 1.2156 | 0.89141
| C.II. | 0.768 | 0.832 | 1.426 | 1.046 |  | C.II. | 0.66027 | 0.71529 | 1.2262 | 0.89922
| C.III. | 0.873 | 0.945 | 1.621 | 1.188 |  | C.III. | 0.75044 | 0.81297 | 1.3937 | 1.022

## Summary of SF of 1 or more
Scenarios Per Configuration and Key Design Features |  |  | SF(excluding losses) Value
• DE absorption chillers with ETCs: Rooftops only | A.I | Rooftop use factor of 0.60 | 1.0028
•DE absorption chillers with ETCs: Rooftops & Façade | C.I | Rooftop use factor of 0.40 | 1.0792
|  | Rooftop use factor of 0.50 | 1.2463
|  | Rooftop use factor of 0.6 | 1.4134
| C.II | Rooftop use factor of 0.40 &Overhang (tilt angel of 60) | 1.0885
|  | Rooftop use factor of 0.40 &Overhang (tilt angel of 30) | 1.091
|  | Rooftop use factor of 0.40 &Overhang (tilt angel of 0) | 1.0916
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 60) | 1.2556
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 30) | 1.2581
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 0) | 1.2587
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 60) | 1.4228
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 30) | 1.4253
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 0) | 1.4258
| C.III | Rooftop use factor of 0.25 &Overhang (tilt angel of 60) | 1.0325
|  | Rooftop use factor of 0.25 &Overhang (tilt angel of 30) | 1.035
|  | Rooftop use factor of 0.25 &Overhang (tilt angel of 0) | 1.0356
|  | Rooftop use factor of 0.40 &Overhang (tilt angel of 60) | 1.2832
|  | Rooftop use factor of 0.40 &Overhang (tilt angel of 30) | 1.2857
|  | Rooftop use factor of 0.40 &Overhang (tilt angel of 0) | 1.2863
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 60) | 1.4503
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 30) | 1.4529
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 0) | 1.4534
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 60) | 1.6175
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 30) | 1.62
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 0) | 1.6205
•Water-cooled VCC and PV panels: Rooftops & Façade | C.I | Rooftop use factor of 0.6 | 1.0365
| C.II | Rooftop use factor of 0.60 &Overhang (tilt angel of 60) | 1.0434
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 30) | 1.0452
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 0) | 1.0456
| C.III | Rooftop use factor of 0.50 &Overhang (tilt angel of 60) | 1.0636
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 30) | 1.0654
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 0) | 1.0658
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 60) | 1.1861
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 30) | 1.188
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 0) | 1.1884
Scenarios Per Configuration and Key Design Features |  |  | SF(including losses) Value
•DE absorption chillers with ETCs: Rooftops & Façade | C.I | Rooftop use factor of 0.50 | 1.0718
|  | Rooftop use factor of 0.6 | 1.2156
| C.II | Rooftop use factor of 0.50 &Overhang (tilt angel of 60) | 1.0798
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 30) | 1.082
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 0) | 1.0825
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 60) | 1.2236
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 30) | 1.2257
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 0) | 1.2262
| C.III | Rooftop use factor of 0.40 &Overhang (tilt angel of 60) | 1.1036
|  | Rooftop use factor of 0.40 &Overhang (tilt angel of 30) | 1.1057
|  | Rooftop use factor of 0.40 &Overhang (tilt angel of 0) | 1.1062
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 60) | 1.2473
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 30) | 1.2495
|  | Rooftop use factor of 0.50 &Overhang (tilt angel of 0) | 1.2499
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 60) | 1.391
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 30) | 1.3932
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 0) | 1.3937
•Water-cooled VCC and PV panels: Rooftops & Façade | C.III | Rooftop use factor of 0.60 &Overhang (tilt angel of 60) | 1.0201
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 30) | 1.0217
|  | Rooftop use factor of 0.60 &Overhang (tilt angel of 0) | 1.022